## How Many Days
How long will it take for my water storage to reach freezing temperatures? | [8 empty] | Initial Heat in tank (BTU) | 51460
Note: Cylindrical Tank Calculations; Non-windy conditions only. | [8 empty] | Heat in water = 8.3 BTU/degF-Gal
User Inputs
Tank Size (gal) | 1550 | [7 empty] | rb | 3.625 | ft
Temperature of water at fillup (deg F) | 36 | [7 empty] | rc | 3.7917 | ft
Freezing Temp (deg F) | 32 | [7 empty] | ln(rc/rb) | 0.044951 | unitless
Outside temp (deg F) | -40 | [7 empty] | kinsulation | 0.013889 | (BTU-ft/(hr-ft2-F)
Height of tank (ft) | 5.4167 | [7 empty] | GrPr (air, -40F) | 10^10
Diameter of Tank (ft) | 7.25 | [7 empty] | h (cylinder) | 0.80481
R-value per inch of Insulation | 6 | [7 empty] | Thermal conductivity of insulation (BTU-ft/(hr-ft2-F) | 0.013889
Thickness of insulation (inches) | 2
How much heat was lost during this time? (total BTUs) | 51460
How many hours until danger zone? | 41
How many days? | 1.7083
If "#N/A" appears, adjust outside temp and or Insulation values.
| Time (hrs) | T1 | Heat lost to environment (BTU/hr) | Temperature of water after 1 hr | Rounded Temp (F) | Time (hrs) | Time (days)
| 0 | 36 | 1245.5671 | 35.9032 | 35.9 | 0 | 0
| 1 | 35.9032 | 1243.9803 | 35.8065 | 35.8 | 1 | 0.041667
| 2 | 35.8065 | 1242.3956 | 35.7099 | 35.7 | 2 | 0.083333
| 3 | 35.7099 | 1240.8129 | 35.6135 | 35.6 | 3 | 0.125
| 4 | 35.6135 | 1239.2322 | 35.5171 | 35.5 | 4 | 0.16667
| 5 | 35.5171 | 1237.6535 | 35.4209 | 35.4 | 5 | 0.20833
| 6 | 35.4209 | 1236.0768 | 35.3249 | 35.3 | 6 | 0.25
| 7 | 35.3249 | 1234.5021 | 35.2289 | 35.2 | 7 | 0.29167
| 8 | 35.2289 | 1232.9295 | 35.1331 | 35.1 | 8 | 0.33333
| 9 | 35.1331 | 1231.3588 | 35.0373 | 35 | 9 | 0.375
| 10 | 35.0373 | 1229.7902 | 34.9418 | 34.9 | 10 | 0.41667
| 11 | 34.9418 | 1228.2235 | 34.8463 | 34.8 | 11 | 0.45833
| 12 | 34.8463 | 1226.6588 | 34.7509 | 34.8 | 12 | 0.5
| 13 | 34.7509 | 1225.0962 | 34.6557 | 34.7 | 13 | 0.54167
| 14 | 34.6557 | 1223.5355 | 34.5606 | 34.6 | 14 | 0.58333
| 15 | 34.5606 | 1221.9768 | 34.4656 | 34.5 | 15 | 0.625
| 16 | 34.4656 | 1220.4201 | 34.3708 | 34.4 | 16 | 0.66667
| 17 | 34.3708 | 1218.8654 | 34.276 | 34.3 | 17 | 0.70833
| 18 | 34.276 | 1217.3126 | 34.1814 | 34.2 | 18 | 0.75
| 19 | 34.1814 | 1215.7619 | 34.0869 | 34.1 | 19 | 0.79167
| 20 | 34.0869 | 1214.2131 | 33.9925 | 34 | 20 | 0.83333
| 21 | 33.9925 | 1212.6663 | 33.8982 | 33.9 | 21 | 0.875
| 22 | 33.8982 | 1211.1214 | 33.8041 | 33.8 | 22 | 0.91667
| 23 | 33.8041 | 1209.5785 | 33.7101 | 33.7 | 23 | 0.95833
| 24 | 33.7101 | 1208.0376 | 33.6162 | 33.6 | 24 | 1
| 25 | 33.6162 | 1206.4987 | 33.5224 | 33.5 | 25 | 1.0417
| 26 | 33.5224 | 1204.9617 | 33.4287 | 33.4 | 26 | 1.0833
| 27 | 33.4287 | 1203.4267 | 33.3352 | 33.3 | 27 | 1.125
| 28 | 33.3352 | 1201.8936 | 33.2418 | 33.2 | 28 | 1.1667
| 29 | 33.2418 | 1200.3625 | 33.1485 | 33.1 | 29 | 1.2083
| 30 | 33.1485 | 1198.8333 | 33.0553 | 33.1 | 30 | 1.25
| 31 | 33.0553 | 1197.3061 | 32.9622 | 33 | 31 | 1.2917
| 32 | 32.9622 | 1195.7808 | 32.8693 | 32.9 | 32 | 1.3333
| 33 | 32.8693 | 1194.2574 | 32.7764 | 32.8 | 33 | 1.375
| 34 | 32.7764 | 1192.7361 | 32.6837 | 32.7 | 34 | 1.4167
| 35 | 32.6837 | 1191.2166 | 32.5911 | 32.6 | 35 | 1.4583
| 36 | 32.5911 | 1189.6991 | 32.4987 | 32.5 | 36 | 1.5
| 37 | 32.4987 | 1188.1835 | 32.4063 | 32.4 | 37 | 1.5417
| 38 | 32.4063 | 1186.6698 | 32.3141 | 32.3 | 38 | 1.5833
| 39 | 32.3141 | 1185.1581 | 32.2219 | 32.2 | 39 | 1.625
| 40 | 32.2219 | 1183.6483 | 32.1299 | 32.1 | 40 | 1.6667
| 41 | 32.1299 | 1182.1404 | 32.038 | 32 | 41 | 1.7083
| 42 | 32.038 | 1180.6345 | 31.9463 | 31.9 | 42 | 1.75
| 43 | 31.9463 | 1179.1304 | 31.8546 | 31.9 | 43 | 1.7917
| 44 | 31.8546 | 1177.6283 | 31.7631 | 31.8 | 44 | 1.8333
| 45 | 31.7631 | 1176.1281 | 31.6717 | 31.7 | 45 | 1.875
| 46 | 31.6717 | 1174.6298 | 31.5804 | 31.6 | 46 | 1.9167
| 47 | 31.5804 | 1173.1334 | 31.4892 | 31.5 | 47 | 1.9583
| 48 | 31.4892 | 1171.6389 | 31.3981 | 31.4 | 48 | 2
| 49 | 31.3981 | 1170.1463 | 31.3071 | 31.3 | 49 | 2.0417
| 50 | 31.3071 | 1168.6557 | 31.2163 | 31.2 | 50 | 2.0833
| 51 | 31.2163 | 1167.1669 | 31.1256 | 31.1 | 51 | 2.125
| 52 | 31.1256 | 1165.68 | 31.035 | 31 | 52 | 2.1667
| 53 | 31.035 | 1164.195 | 30.9445 | 30.9 | 53 | 2.2083
| 54 | 30.9445 | 1162.7119 | 30.8541 | 30.9 | 54 | 2.25
| 55 | 30.8541 | 1161.2307 | 30.7638 | 30.8 | 55 | 2.2917
| 56 | 30.7638 | 1159.7514 | 30.6737 | 30.7 | 56 | 2.3333
| 57 | 30.6737 | 1158.274 | 30.5837 | 30.6 | 57 | 2.375
| 58 | 30.5837 | 1156.7984 | 30.4937 | 30.5 | 58 | 2.4167
| 59 | 30.4937 | 1155.3247 | 30.4039 | 30.4 | 59 | 2.4583
| 60 | 30.4039 | 1153.8529 | 30.3142 | 30.3 | 60 | 2.5
| 61 | 30.3142 | 1152.383 | 30.2247 | 30.2 | 61 | 2.5417
| 62 | 30.2247 | 1150.915 | 30.1352 | 30.1 | 62 | 2.5833
| 63 | 30.1352 | 1149.4488 | 30.0459 | 30 | 63 | 2.625
| 64 | 30.0459 | 1147.9845 | 29.9566 | 30 | 64 | 2.6667
| 65 | 29.9566 | 1146.522 | 29.8675 | 29.9 | 65 | 2.7083
| 66 | 29.8675 | 1145.0614 | 29.7785 | 29.8 | 66 | 2.75
| 67 | 29.7785 | 1143.6027 | 29.6896 | 29.7 | 67 | 2.7917
| 68 | 29.6896 | 1142.1459 | 29.6008 | 29.6 | 68 | 2.8333
| 69 | 29.6008 | 1140.6908 | 29.5122 | 29.5 | 69 | 2.875
| 70 | 29.5122 | 1139.2377 | 29.4236 | 29.4 | 70 | 2.9167
| 71 | 29.4236 | 1137.7864 | 29.3352 | 29.3 | 71 | 2.9583
| 72 | 29.3352 | 1136.3369 | 29.2468 | 29.2 | 72 | 3
| 73 | 29.2468 | 1134.8893 | 29.1586 | 29.2 | 73 | 3.0417
| 74 | 29.1586 | 1133.4436 | 29.0705 | 29.1 | 74 | 3.0833
| 75 | 29.0705 | 1131.9996 | 28.9825 | 29 | 75 | 3.125
| 76 | 28.9825 | 1130.5576 | 28.8947 | 28.9 | 76 | 3.1667
| 77 | 28.8947 | 1129.1173 | 28.8069 | 28.8 | 77 | 3.2083
| 78 | 28.8069 | 1127.6789 | 28.7192 | 28.7 | 78 | 3.25
| 79 | 28.7192 | 1126.2423 | 28.6317 | 28.6 | 79 | 3.2917
| 80 | 28.6317 | 1124.8076 | 28.5443 | 28.5 | 80 | 3.3333
| 81 | 28.5443 | 1123.3747 | 28.4569 | 28.5 | 81 | 3.375
| 82 | 28.4569 | 1121.9436 | 28.3697 | 28.4 | 82 | 3.4167
| 83 | 28.3697 | 1120.5143 | 28.2826 | 28.3 | 83 | 3.4583
| 84 | 28.2826 | 1119.0868 | 28.1956 | 28.2 | 84 | 3.5
| 85 | 28.1956 | 1117.6612 | 28.1088 | 28.1 | 85 | 3.5417
| 86 | 28.1088 | 1116.2374 | 28.022 | 28 | 86 | 3.5833
| 87 | 28.022 | 1114.8154 | 27.9353 | 27.9 | 87 | 3.625
| 88 | 27.9353 | 1113.3952 | 27.8488 | 27.8 | 88 | 3.6667
| 89 | 27.8488 | 1111.9768 | 27.7624 | 27.8 | 89 | 3.7083
| 90 | 27.7624 | 1110.5602 | 27.676 | 27.7 | 90 | 3.75
| 91 | 27.676 | 1109.1455 | 27.5898 | 27.6 | 91 | 3.7917
| 92 | 27.5898 | 1107.7325 | 27.5037 | 27.5 | 92 | 3.8333
| 93 | 27.5037 | 1106.3213 | 27.4177 | 27.4 | 93 | 3.875
| 94 | 27.4177 | 1104.912 | 27.3318 | 27.3 | 94 | 3.9167
| 95 | 27.3318 | 1103.5044 | 27.2461 | 27.2 | 95 | 3.9583
| 96 | 27.2461 | 1102.0986 | 27.1604 | 27.2 | 96 | 4
| 97 | 27.1604 | 1100.6946 | 27.0748 | 27.1 | 97 | 4.0417
| 98 | 27.0748 | 1099.2924 | 26.9894 | 27 | 98 | 4.0833
| 99 | 26.9894 | 1097.892 | 26.9041 | 26.9 | 99 | 4.125
| 100 | 26.9041 | 1096.4934 | 26.8188 | 26.8 | 100 | 4.1667
| 101 | 26.8188 | 1095.0965 | 26.7337 | 26.7 | 101 | 4.2083
| 102 | 26.7337 | 1093.7015 | 26.6487 | 26.6 | 102 | 4.25
| 103 | 26.6487 | 1092.3082 | 26.5638 | 26.6 | 103 | 4.2917
| 104 | 26.5638 | 1090.9166 | 26.479 | 26.5 | 104 | 4.3333
| 105 | 26.479 | 1089.5269 | 26.3943 | 26.4 | 105 | 4.375
| 106 | 26.3943 | 1088.1389 | 26.3097 | 26.3 | 106 | 4.4167
| 107 | 26.3097 | 1086.7527 | 26.2252 | 26.2 | 107 | 4.4583
| 108 | 26.2252 | 1085.3683 | 26.1409 | 26.1 | 108 | 4.5
| 109 | 26.1409 | 1083.9856 | 26.0566 | 26.1 | 109 | 4.5417
| 110 | 26.0566 | 1082.6047 | 25.9725 | 26 | 110 | 4.5833
| 111 | 25.9725 | 1081.2255 | 25.8884 | 25.9 | 111 | 4.625
| 112 | 25.8884 | 1079.8481 | 25.8045 | 25.8 | 112 | 4.6667
| 113 | 25.8045 | 1078.4725 | 25.7207 | 25.7 | 113 | 4.7083
| 114 | 25.7207 | 1077.0986 | 25.6369 | 25.6 | 114 | 4.75
| 115 | 25.6369 | 1075.7264 | 25.5533 | 25.6 | 115 | 4.7917
| 116 | 25.5533 | 1074.356 | 25.4698 | 25.5 | 116 | 4.8333
| 117 | 25.4698 | 1072.9874 | 25.3864 | 25.4 | 117 | 4.875
| 118 | 25.3864 | 1071.6205 | 25.3031 | 25.3 | 118 | 4.9167
| 119 | 25.3031 | 1070.2553 | 25.2199 | 25.2 | 119 | 4.9583
| 120 | 25.2199 | 1068.8919 | 25.1368 | 25.1 | 120 | 5
| 121 | 25.1368 | 1067.5302 | 25.0539 | 25.1 | 121 | 5.0417
| 122 | 25.0539 | 1066.1703 | 24.971 | 25 | 122 | 5.0833
| 123 | 24.971 | 1064.812 | 24.8882 | 24.9 | 123 | 5.125
| 124 | 24.8882 | 1063.4556 | 24.8055 | 24.8 | 124 | 5.1667
| 125 | 24.8055 | 1062.1008 | 24.723 | 24.7 | 125 | 5.2083
| 126 | 24.723 | 1060.7478 | 24.6405 | 24.6 | 126 | 5.25
| 127 | 24.6405 | 1059.3964 | 24.5582 | 24.6 | 127 | 5.2917
| 128 | 24.5582 | 1058.0469 | 24.476 | 24.5 | 128 | 5.3333
| 129 | 24.476 | 1056.699 | 24.3938 | 24.4 | 129 | 5.375
| 130 | 24.3938 | 1055.3528 | 24.3118 | 24.3 | 130 | 5.4167
| 131 | 24.3118 | 1054.0084 | 24.2299 | 24.2 | 131 | 5.4583
| 132 | 24.2299 | 1052.6657 | 24.148 | 24.1 | 132 | 5.5
| 133 | 24.148 | 1051.3246 | 24.0663 | 24.1 | 133 | 5.5417
| 134 | 24.0663 | 1049.9853 | 23.9847 | 24 | 134 | 5.5833
| 135 | 23.9847 | 1048.6477 | 23.9032 | 23.9 | 135 | 5.625
| 136 | 23.9032 | 1047.3118 | 23.8218 | 23.8 | 136 | 5.6667
| 137 | 23.8218 | 1045.9776 | 23.7405 | 23.7 | 137 | 5.7083
| 138 | 23.7405 | 1044.6451 | 23.6593 | 23.7 | 138 | 5.75
| 139 | 23.6593 | 1043.3143 | 23.5782 | 23.6 | 139 | 5.7917
| 140 | 23.5782 | 1041.9852 | 23.4972 | 23.5 | 140 | 5.8333
| 141 | 23.4972 | 1040.6578 | 23.4163 | 23.4 | 141 | 5.875
| 142 | 23.4163 | 1039.3321 | 23.3355 | 23.3 | 142 | 5.9167
| 143 | 23.3355 | 1038.0081 | 23.2548 | 23.3 | 143 | 5.9583
| 144 | 23.2548 | 1036.6857 | 23.1742 | 23.2 | 144 | 6
| 145 | 23.1742 | 1035.3651 | 23.0938 | 23.1 | 145 | 6.0417
| 146 | 23.0938 | 1034.0461 | 23.0134 | 23 | 146 | 6.0833
| 147 | 23.0134 | 1032.7288 | 22.9331 | 22.9 | 147 | 6.125
| 148 | 22.9331 | 1031.4132 | 22.8529 | 22.9 | 148 | 6.1667
| 149 | 22.8529 | 1030.0992 | 22.7729 | 22.8 | 149 | 6.2083
| 150 | 22.7729 | 1028.787 | 22.6929 | 22.7 | 150 | 6.25
| 151 | 22.6929 | 1027.4764 | 22.613 | 22.6 | 151 | 6.2917
| 152 | 22.613 | 1026.1674 | 22.5333 | 22.5 | 152 | 6.3333
| 153 | 22.5333 | 1024.8602 | 22.4536 | 22.5 | 153 | 6.375
| 154 | 22.4536 | 1023.5546 | 22.374 | 22.4 | 154 | 6.4167
| 155 | 22.374 | 1022.2507 | 22.2946 | 22.3 | 155 | 6.4583
| 156 | 22.2946 | 1020.9484 | 22.2152 | 22.2 | 156 | 6.5
| 157 | 22.2152 | 1019.6478 | 22.136 | 22.1 | 157 | 6.5417
| 158 | 22.136 | 1018.3488 | 22.0568 | 22.1 | 158 | 6.5833
| 159 | 22.0568 | 1017.0515 | 21.9778 | 22 | 159 | 6.625
| 160 | 21.9778 | 1015.7559 | 21.8988 | 21.9 | 160 | 6.6667
| 161 | 21.8988 | 1014.4619 | 21.8199 | 21.8 | 161 | 6.7083
| 162 | 21.8199 | 1013.1695 | 21.7412 | 21.7 | 162 | 6.75
| 163 | 21.7412 | 1011.8788 | 21.6625 | 21.7 | 163 | 6.7917
| 164 | 21.6625 | 1010.5898 | 21.584 | 21.6 | 164 | 6.8333
| 165 | 21.584 | 1009.3024 | 21.5055 | 21.5 | 165 | 6.875
40 | 166 | 21.5055 | 1008.0166 | 21.4272 | 21.4 | 166 | 6.9167
#N/A | 167 | 21.4272 | 1006.7324 | 21.3489 | 21.3 | 167 | 6.9583
41 | 168 | 21.3489 | 1005.4499 | 21.2708 | 21.3 | 168 | 7
| 169 | 21.2708 | 1004.1691 | 21.1927 | 21.2 | 169 | 7.0417
| 170 | 21.1927 | 1002.8898 | 21.1148 | 21.1 | 170 | 7.0833
| 171 | 21.1148 | 1001.6122 | 21.0369 | 21 | 171 | 7.125
| 172 | 21.0369 | 1000.3363 | 20.9591 | 21 | 172 | 7.1667
| 173 | 20.9591 | 999.0619 | 20.8815 | 20.9 | 173 | 7.2083
| 174 | 20.8815 | 997.7892 | 20.8039 | 20.8 | 174 | 7.25
| 175 | 20.8039 | 996.5181 | 20.7265 | 20.7 | 175 | 7.2917
| 176 | 20.7265 | 995.2486 | 20.6491 | 20.6 | 176 | 7.3333
| 177 | 20.6491 | 993.9807 | 20.5718 | 20.6 | 177 | 7.375
| 178 | 20.5718 | 992.7144 | 20.4947 | 20.5 | 178 | 7.4167
| 179 | 20.4947 | 991.4498 | 20.4176 | 20.4 | 179 | 7.4583
| 180 | 20.4176 | 990.1868 | 20.3406 | 20.3 | 180 | 7.5
| 181 | 20.3406 | 988.9253 | 20.2638 | 20.3 | 181 | 7.5417
| 182 | 20.2638 | 987.6655 | 20.187 | 20.2 | 182 | 7.5833
| 183 | 20.187 | 986.4073 | 20.1103 | 20.1 | 183 | 7.625
| 184 | 20.1103 | 985.1507 | 20.0338 | 20 | 184 | 7.6667
| 185 | 20.0338 | 983.8957 | 19.9573 | 20 | 185 | 7.7083
| 186 | 19.9573 | 982.6423 | 19.8809 | 19.9 | 186 | 7.75
| 187 | 19.8809 | 981.3905 | 19.8046 | 19.8 | 187 | 7.7917
| 188 | 19.8046 | 980.1403 | 19.7284 | 19.7 | 188 | 7.8333
| 189 | 19.7284 | 978.8916 | 19.6523 | 19.7 | 189 | 7.875
| 190 | 19.6523 | 977.6446 | 19.5763 | 19.6 | 190 | 7.9167
| 191 | 19.5763 | 976.3992 | 19.5005 | 19.5 | 191 | 7.9583
| 192 | 19.5005 | 975.1553 | 19.4247 | 19.4 | 192 | 8
| 193 | 19.4247 | 973.913 | 19.3489 | 19.3 | 193 | 8.0417
| 194 | 19.3489 | 972.6723 | 19.2733 | 19.3 | 194 | 8.0833
| 195 | 19.2733 | 971.4332 | 19.1978 | 19.2 | 195 | 8.125
| 196 | 19.1978 | 970.1957 | 19.1224 | 19.1 | 196 | 8.1667
| 197 | 19.1224 | 968.9597 | 19.0471 | 19 | 197 | 8.2083
| 198 | 19.0471 | 967.7254 | 18.9719 | 19 | 198 | 8.25
| 199 | 18.9719 | 966.4925 | 18.8968 | 18.9 | 199 | 8.2917
| 200 | 18.8968 | 965.2613 | 18.8217 | 18.8 | 200 | 8.3333
| 201 | 18.8217 | 964.0316 | 18.7468 | 18.7 | 201 | 8.375
| 202 | 18.7468 | 962.8035 | 18.672 | 18.7 | 202 | 8.4167
| 203 | 18.672 | 961.577 | 18.5972 | 18.6 | 203 | 8.4583
| 204 | 18.5972 | 960.352 | 18.5226 | 18.5 | 204 | 8.5
| 205 | 18.5226 | 959.1286 | 18.448 | 18.4 | 205 | 8.5417
| 206 | 18.448 | 957.9067 | 18.3735 | 18.4 | 206 | 8.5833
| 207 | 18.3735 | 956.6864 | 18.2992 | 18.3 | 207 | 8.625
| 208 | 18.2992 | 955.4677 | 18.2249 | 18.2 | 208 | 8.6667
| 209 | 18.2249 | 954.2505 | 18.1507 | 18.2 | 209 | 8.7083
| 210 | 18.1507 | 953.0349 | 18.0767 | 18.1 | 210 | 8.75
| 211 | 18.0767 | 951.8208 | 18.0027 | 18 | 211 | 8.7917
| 212 | 18.0027 | 950.6082 | 17.9288 | 17.9 | 212 | 8.8333
| 213 | 17.9288 | 949.3972 | 17.855 | 17.9 | 213 | 8.875
| 214 | 17.855 | 948.1877 | 17.7813 | 17.8 | 214 | 8.9167
| 215 | 17.7813 | 946.9798 | 17.7077 | 17.7 | 215 | 8.9583
| 216 | 17.7077 | 945.7734 | 17.6342 | 17.6 | 216 | 9
| 217 | 17.6342 | 944.5686 | 17.5607 | 17.6 | 217 | 9.0417
| 218 | 17.5607 | 943.3653 | 17.4874 | 17.5 | 218 | 9.0833
| 219 | 17.4874 | 942.1635 | 17.4142 | 17.4 | 219 | 9.125
| 220 | 17.4142 | 940.9633 | 17.341 | 17.3 | 220 | 9.1667
| 221 | 17.341 | 939.7646 | 17.268 | 17.3 | 221 | 9.2083
| 222 | 17.268 | 938.5674 | 17.195 | 17.2 | 222 | 9.25
| 223 | 17.195 | 937.3717 | 17.1222 | 17.1 | 223 | 9.2917
| 224 | 17.1222 | 936.1776 | 17.0494 | 17 | 224 | 9.3333
| 225 | 17.0494 | 934.9849 | 16.9767 | 17 | 225 | 9.375
| 226 | 16.9767 | 933.7938 | 16.9041 | 16.9 | 226 | 9.4167
| 227 | 16.9041 | 932.6043 | 16.8316 | 16.8 | 227 | 9.4583
| 228 | 16.8316 | 931.4162 | 16.7592 | 16.8 | 228 | 9.5
| 229 | 16.7592 | 930.2296 | 16.6869 | 16.7 | 229 | 9.5417
| 230 | 16.6869 | 929.0446 | 16.6147 | 16.6 | 230 | 9.5833
| 231 | 16.6147 | 927.8611 | 16.5426 | 16.5 | 231 | 9.625
| 232 | 16.5426 | 926.679 | 16.4706 | 16.5 | 232 | 9.6667
| 233 | 16.4706 | 925.4985 | 16.3986 | 16.4 | 233 | 9.7083
| 234 | 16.3986 | 924.3195 | 16.3268 | 16.3 | 234 | 9.75
| 235 | 16.3268 | 923.142 | 16.255 | 16.3 | 235 | 9.7917
| 236 | 16.255 | 921.966 | 16.1834 | 16.2 | 236 | 9.8333
| 237 | 16.1834 | 920.7915 | 16.1118 | 16.1 | 237 | 9.875
| 238 | 16.1118 | 919.6184 | 16.0403 | 16 | 238 | 9.9167
| 239 | 16.0403 | 918.4469 | 15.9689 | 16 | 239 | 9.9583
| 240 | 15.9689 | 917.2769 | 15.8976 | 15.9 | 240 | 10
| 241 | 15.8976 | 916.1083 | 15.8264 | 15.8 | 241 | 10.0417
| 242 | 15.8264 | 914.9413 | 15.7553 | 15.8 | 242 | 10.0833
| 243 | 15.7553 | 913.7757 | 15.6843 | 15.7 | 243 | 10.125
| 244 | 15.6843 | 912.6116 | 15.6133 | 15.6 | 244 | 10.1667
| 245 | 15.6133 | 911.449 | 15.5425 | 15.5 | 245 | 10.2083
| 246 | 15.5425 | 910.2879 | 15.4717 | 15.5 | 246 | 10.25
| 247 | 15.4717 | 909.1283 | 15.4011 | 15.4 | 247 | 10.2917
| 248 | 15.4011 | 907.9701 | 15.3305 | 15.3 | 248 | 10.3333
| 249 | 15.3305 | 906.8134 | 15.26 | 15.3 | 249 | 10.375
| 250 | 15.26 | 905.6582 | 15.1896 | 15.2 | 250 | 10.4167
| 251 | 15.1896 | 904.5045 | 15.1193 | 15.1 | 251 | 10.4583
| 252 | 15.1193 | 903.3522 | 15.0491 | 15 | 252 | 10.5
| 253 | 15.0491 | 902.2014 | 14.9789 | 15 | 253 | 10.5417
| 254 | 14.9789 | 901.0521 | 14.9089 | 14.9 | 254 | 10.5833
| 255 | 14.9089 | 899.9042 | 14.839 | 14.8 | 255 | 10.625
| 256 | 14.839 | 898.7578 | 14.7691 | 14.8 | 256 | 10.6667
| 257 | 14.7691 | 897.6128 | 14.6993 | 14.7 | 257 | 10.7083
| 258 | 14.6993 | 896.4694 | 14.6296 | 14.6 | 258 | 10.75
| 259 | 14.6296 | 895.3273 | 14.56 | 14.6 | 259 | 10.7917
| 260 | 14.56 | 894.1867 | 14.4905 | 14.5 | 260 | 10.8333
| 261 | 14.4905 | 893.0476 | 14.4211 | 14.4 | 261 | 10.875
| 262 | 14.4211 | 891.9099 | 14.3518 | 14.4 | 262 | 10.9167
| 263 | 14.3518 | 890.7737 | 14.2826 | 14.3 | 263 | 10.9583
| 264 | 14.2826 | 889.6389 | 14.2134 | 14.2 | 264 | 11
| 265 | 14.2134 | 888.5056 | 14.1443 | 14.1 | 265 | 11.0417
| 266 | 14.1443 | 887.3737 | 14.0754 | 14.1 | 266 | 11.0833
| 267 | 14.0754 | 886.2433 | 14.0065 | 14 | 267 | 11.125
| 268 | 14.0065 | 885.1143 | 13.9377 | 13.9 | 268 | 11.1667
| 269 | 13.9377 | 883.9867 | 13.869 | 13.9 | 269 | 11.2083
| 270 | 13.869 | 882.8606 | 13.8003 | 13.8 | 270 | 11.25
| 271 | 13.8003 | 881.7359 | 13.7318 | 13.7 | 271 | 11.2917
| 272 | 13.7318 | 880.6126 | 13.6633 | 13.7 | 272 | 11.3333
| 273 | 13.6633 | 879.4908 | 13.595 | 13.6 | 273 | 11.375
| 274 | 13.595 | 878.3704 | 13.5267 | 13.5 | 274 | 11.4167
| 275 | 13.5267 | 877.2514 | 13.4585 | 13.5 | 275 | 11.4583
| 276 | 13.4585 | 876.1338 | 13.3904 | 13.4 | 276 | 11.5
| 277 | 13.3904 | 875.0177 | 13.3224 | 13.3 | 277 | 11.5417
| 278 | 13.3224 | 873.903 | 13.2545 | 13.3 | 278 | 11.5833
| 279 | 13.2545 | 872.7897 | 13.1866 | 13.2 | 279 | 11.625
| 280 | 13.1866 | 871.6778 | 13.1189 | 13.1 | 280 | 11.6667
| 281 | 13.1189 | 870.5674 | 13.0512 | 13.1 | 281 | 11.7083
| 282 | 13.0512 | 869.4583 | 12.9836 | 13 | 282 | 11.75
| 283 | 12.9836 | 868.3507 | 12.9161 | 12.9 | 283 | 11.7917
| 284 | 12.9161 | 867.2445 | 12.8487 | 12.8 | 284 | 11.8333
| 285 | 12.8487 | 866.1397 | 12.7814 | 12.8 | 285 | 11.875
| 286 | 12.7814 | 865.0363 | 12.7141 | 12.7 | 286 | 11.9167
| 287 | 12.7141 | 863.9343 | 12.647 | 12.6 | 287 | 11.9583
| 288 | 12.647 | 862.8337 | 12.5799 | 12.6 | 288 | 12
| 289 | 12.5799 | 861.7345 | 12.5129 | 12.5 | 289 | 12.0417
| 290 | 12.5129 | 860.6368 | 12.446 | 12.4 | 290 | 12.0833
| 291 | 12.446 | 859.5404 | 12.3792 | 12.4 | 291 | 12.125
| 292 | 12.3792 | 858.4454 | 12.3125 | 12.3 | 292 | 12.1667
| 293 | 12.3125 | 857.3518 | 12.2459 | 12.2 | 293 | 12.2083
| 294 | 12.2459 | 856.2596 | 12.1793 | 12.2 | 294 | 12.25
| 295 | 12.1793 | 855.1688 | 12.1128 | 12.1 | 295 | 12.2917
| 296 | 12.1128 | 854.0794 | 12.0464 | 12 | 296 | 12.3333
| 297 | 12.0464 | 852.9913 | 11.9801 | 12 | 297 | 12.375
| 298 | 11.9801 | 851.9047 | 11.9139 | 11.9 | 298 | 12.4167
| 299 | 11.9139 | 850.8194 | 11.8478 | 11.8 | 299 | 12.4583
| 300 | 11.8478 | 849.7355 | 11.7817 | 11.8 | 300 | 12.5
| 301 | 11.7817 | 848.653 | 11.7158 | 11.7 | 301 | 12.5417
| 302 | 11.7158 | 847.5719 | 11.6499 | 11.6 | 302 | 12.5833
| 303 | 11.6499 | 846.4922 | 11.5841 | 11.6 | 303 | 12.625
| 304 | 11.5841 | 845.4138 | 11.5184 | 11.5 | 304 | 12.6667
| 305 | 11.5184 | 844.3368 | 11.4527 | 11.5 | 305 | 12.7083
| 306 | 11.4527 | 843.2612 | 11.3872 | 11.4 | 306 | 12.75
| 307 | 11.3872 | 842.1869 | 11.3217 | 11.3 | 307 | 12.7917
| 308 | 11.3217 | 841.1141 | 11.2564 | 11.3 | 308 | 12.8333
| 309 | 11.2564 | 840.0425 | 11.1911 | 11.2 | 309 | 12.875
| 310 | 11.1911 | 838.9724 | 11.1258 | 11.1 | 310 | 12.9167
| 311 | 11.1258 | 837.9036 | 11.0607 | 11.1 | 311 | 12.9583
| 312 | 11.0607 | 836.8362 | 10.9957 | 11 | 312 | 13
| 313 | 10.9957 | 835.7701 | 10.9307 | 10.9 | 313 | 13.0417
| 314 | 10.9307 | 834.7054 | 10.8658 | 10.9 | 314 | 13.0833
| 315 | 10.8658 | 833.6421 | 10.801 | 10.8 | 315 | 13.125
| 316 | 10.801 | 832.5801 | 10.7363 | 10.7 | 316 | 13.1667
| 317 | 10.7363 | 831.5194 | 10.6717 | 10.7 | 317 | 13.2083
| 318 | 10.6717 | 830.4601 | 10.6071 | 10.6 | 318 | 13.25
| 319 | 10.6071 | 829.4022 | 10.5427 | 10.5 | 319 | 13.2917
| 320 | 10.5427 | 828.3456 | 10.4783 | 10.5 | 320 | 13.3333
| 321 | 10.4783 | 827.2903 | 10.414 | 10.4 | 321 | 13.375
| 322 | 10.414 | 826.2364 | 10.3497 | 10.3 | 322 | 13.4167
| 323 | 10.3497 | 825.1839 | 10.2856 | 10.3 | 323 | 13.4583
| 324 | 10.2856 | 824.1326 | 10.2215 | 10.2 | 324 | 13.5
| 325 | 10.2215 | 823.0828 | 10.1576 | 10.2 | 325 | 13.5417
| 326 | 10.1576 | 822.0342 | 10.0937 | 10.1 | 326 | 13.5833
| 327 | 10.0937 | 820.987 | 10.0298 | 10 | 327 | 13.625
| 328 | 10.0298 | 819.9411 | 9.9661 | 10 | 328 | 13.6667
| 329 | 9.9661 | 818.8966 | 9.9025 | 9.9 | 329 | 13.7083
| 330 | 9.9025 | 817.8534 | 9.8389 | 9.8 | 330 | 13.75
| 331 | 9.8389 | 816.8115 | 9.7754 | 9.8 | 331 | 13.7917
| 332 | 9.7754 | 815.7709 | 9.712 | 9.7 | 332 | 13.8333
| 333 | 9.712 | 814.7317 | 9.6487 | 9.6 | 333 | 13.875
| 334 | 9.6487 | 813.6938 | 9.5854 | 9.6 | 334 | 13.9167
| 335 | 9.5854 | 812.6572 | 9.5222 | 9.5 | 335 | 13.9583
| 336 | 9.5222 | 811.6219 | 9.4591 | 9.5 | 336 | 14
| 337 | 9.4591 | 810.588 | 9.3961 | 9.4 | 337 | 14.0417
| 338 | 9.3961 | 809.5554 | 9.3332 | 9.3 | 338 | 14.0833
| 339 | 9.3332 | 808.5241 | 9.2704 | 9.3 | 339 | 14.125
| 340 | 9.2704 | 807.4941 | 9.2076 | 9.2 | 340 | 14.1667
| 341 | 9.2076 | 806.4654 | 9.1449 | 9.1 | 341 | 14.2083
| 342 | 9.1449 | 805.438 | 9.0823 | 9.1 | 342 | 14.25
| 343 | 9.0823 | 804.4119 | 9.0198 | 9 | 343 | 14.2917
| 344 | 9.0198 | 803.3872 | 8.9573 | 9 | 344 | 14.3333
| 345 | 8.9573 | 802.3637 | 8.895 | 8.9 | 345 | 14.375
| 346 | 8.895 | 801.3416 | 8.8327 | 8.8 | 346 | 14.4167
| 347 | 8.8327 | 800.3207 | 8.7705 | 8.8 | 347 | 14.4583
| 348 | 8.7705 | 799.3012 | 8.7083 | 8.7 | 348 | 14.5
| 349 | 8.7083 | 798.2829 | 8.6463 | 8.6 | 349 | 14.5417
| 350 | 8.6463 | 797.266 | 8.5843 | 8.6 | 350 | 14.5833
| 351 | 8.5843 | 796.2503 | 8.5224 | 8.5 | 351 | 14.625
| 352 | 8.5224 | 795.2359 | 8.4606 | 8.5 | 352 | 14.6667
| 353 | 8.4606 | 794.2229 | 8.3989 | 8.4 | 353 | 14.7083
| 354 | 8.3989 | 793.2111 | 8.3372 | 8.3 | 354 | 14.75
| 355 | 8.3372 | 792.2006 | 8.2756 | 8.3 | 355 | 14.7917
| 356 | 8.2756 | 791.1914 | 8.2141 | 8.2 | 356 | 14.8333
| 357 | 8.2141 | 790.1835 | 8.1527 | 8.2 | 357 | 14.875
| 358 | 8.1527 | 789.1768 | 8.0914 | 8.1 | 358 | 14.9167
| 359 | 8.0914 | 788.1715 | 8.0301 | 8 | 359 | 14.9583
| 360 | 8.0301 | 787.1674 | 7.9689 | 8 | 360 | 15
| 361 | 7.9689 | 786.1646 | 7.9078 | 7.9 | 361 | 15.0417
| 362 | 7.9078 | 785.1631 | 7.8468 | 7.8 | 362 | 15.0833
| 363 | 7.8468 | 784.1629 | 7.7858 | 7.8 | 363 | 15.125
| 364 | 7.7858 | 783.1639 | 7.725 | 7.7 | 364 | 15.1667
| 365 | 7.725 | 782.1662 | 7.6642 | 7.7 | 365 | 15.2083
| 366 | 7.6642 | 781.1698 | 7.6034 | 7.6 | 366 | 15.25
| 367 | 7.6034 | 780.1746 | 7.5428 | 7.5 | 367 | 15.2917
| 368 | 7.5428 | 779.1808 | 7.4822 | 7.5 | 368 | 15.3333
| 369 | 7.4822 | 778.1881 | 7.4217 | 7.4 | 369 | 15.375
| 370 | 7.4217 | 777.1968 | 7.3613 | 7.4 | 370 | 15.4167
| 371 | 7.3613 | 776.2067 | 7.301 | 7.3 | 371 | 15.4583
| 372 | 7.301 | 775.2179 | 7.2407 | 7.2 | 372 | 15.5
| 373 | 7.2407 | 774.2303 | 7.1806 | 7.2 | 373 | 15.5417
| 374 | 7.1806 | 773.244 | 7.1204 | 7.1 | 374 | 15.5833
| 375 | 7.1204 | 772.2589 | 7.0604 | 7.1 | 375 | 15.625
| 376 | 7.0604 | 771.2751 | 7.0005 | 7 | 376 | 15.6667
| 377 | 7.0005 | 770.2926 | 6.9406 | 6.9 | 377 | 15.7083
| 378 | 6.9406 | 769.3113 | 6.8808 | 6.9 | 378 | 15.75
| 379 | 6.8808 | 768.3313 | 6.8211 | 6.8 | 379 | 15.7917
| 380 | 6.8211 | 767.3525 | 6.7614 | 6.8 | 380 | 15.8333
| 381 | 6.7614 | 766.3749 | 6.7019 | 6.7 | 381 | 15.875
| 382 | 6.7019 | 765.3986 | 6.6424 | 6.6 | 382 | 15.9167
| 383 | 6.6424 | 764.4235 | 6.5829 | 6.6 | 383 | 15.9583
| 384 | 6.5829 | 763.4497 | 6.5236 | 6.5 | 384 | 16
| 385 | 6.5236 | 762.4771 | 6.4643 | 6.5 | 385 | 16.0417
| 386 | 6.4643 | 761.5058 | 6.4051 | 6.4 | 386 | 16.0833
| 387 | 6.4051 | 760.5357 | 6.346 | 6.3 | 387 | 16.125
| 388 | 6.346 | 759.5668 | 6.287 | 6.3 | 388 | 16.1667
| 389 | 6.287 | 758.5992 | 6.228 | 6.2 | 389 | 16.2083
| 390 | 6.228 | 757.6328 | 6.1691 | 6.2 | 390 | 16.25
| 391 | 6.1691 | 756.6676 | 6.1103 | 6.1 | 391 | 16.2917
| 392 | 6.1103 | 755.7037 | 6.0516 | 6.1 | 392 | 16.3333
| 393 | 6.0516 | 754.741 | 5.9929 | 6 | 393 | 16.375
| 394 | 5.9929 | 753.7795 | 5.9343 | 5.9 | 394 | 16.4167
| 395 | 5.9343 | 752.8193 | 5.8758 | 5.9 | 395 | 16.4583
| 396 | 5.8758 | 751.8602 | 5.8173 | 5.8 | 396 | 16.5
| 397 | 5.8173 | 750.9024 | 5.759 | 5.8 | 397 | 16.5417
| 398 | 5.759 | 749.9458 | 5.7007 | 5.7 | 398 | 16.5833
| 399 | 5.7007 | 748.9904 | 5.6425 | 5.6 | 399 | 16.625
| 400 | 5.6425 | 748.0363 | 5.5843 | 5.6 | 400 | 16.6667
| 401 | 5.5843 | 747.0833 | 5.5263 | 5.5 | 401 | 16.7083
| 402 | 5.5263 | 746.1316 | 5.4683 | 5.5 | 402 | 16.75
| 403 | 5.4683 | 745.1811 | 5.4103 | 5.4 | 403 | 16.7917
| 404 | 5.4103 | 744.2318 | 5.3525 | 5.4 | 404 | 16.8333
| 405 | 5.3525 | 743.2837 | 5.2947 | 5.3 | 405 | 16.875
| 406 | 5.2947 | 742.3368 | 5.237 | 5.2 | 406 | 16.9167
| 407 | 5.237 | 741.3911 | 5.1794 | 5.2 | 407 | 16.9583
| 408 | 5.1794 | 740.4467 | 5.1218 | 5.1 | 408 | 17
| 409 | 5.1218 | 739.5034 | 5.0643 | 5.1 | 409 | 17.0417
| 410 | 5.0643 | 738.5613 | 5.0069 | 5 | 410 | 17.0833
| 411 | 5.0069 | 737.6204 | 4.9496 | 4.9 | 411 | 17.125
| 412 | 4.9496 | 736.6808 | 4.8923 | 4.9 | 412 | 17.1667
| 413 | 4.8923 | 735.7423 | 4.8351 | 4.8 | 413 | 17.2083
| 414 | 4.8351 | 734.805 | 4.778 | 4.8 | 414 | 17.25
| 415 | 4.778 | 733.8689 | 4.721 | 4.7 | 415 | 17.2917
| 416 | 4.721 | 732.934 | 4.664 | 4.7 | 416 | 17.3333
| 417 | 4.664 | 732.0003 | 4.6071 | 4.6 | 417 | 17.375
| 418 | 4.6071 | 731.0678 | 4.5503 | 4.6 | 418 | 17.4167
| 419 | 4.5503 | 730.1365 | 4.4935 | 4.5 | 419 | 17.4583
| 420 | 4.4935 | 729.2064 | 4.4369 | 4.4 | 420 | 17.5
| 421 | 4.4369 | 728.2774 | 4.3802 | 4.4 | 421 | 17.5417
| 422 | 4.3802 | 727.3496 | 4.3237 | 4.3 | 422 | 17.5833
| 423 | 4.3237 | 726.423 | 4.2672 | 4.3 | 423 | 17.625
| 424 | 4.2672 | 725.4976 | 4.2108 | 4.2 | 424 | 17.6667
| 425 | 4.2108 | 724.5734 | 4.1545 | 4.2 | 425 | 17.7083
| 426 | 4.1545 | 723.6503 | 4.0983 | 4.1 | 426 | 17.75
| 427 | 4.0983 | 722.7285 | 4.0421 | 4 | 427 | 17.7917
| 428 | 4.0421 | 721.8078 | 3.986 | 4 | 428 | 17.8333
| 429 | 3.986 | 720.8882 | 3.93 | 3.9 | 429 | 17.875
| 430 | 3.93 | 719.9699 | 3.874 | 3.9 | 430 | 17.9167
| 431 | 3.874 | 719.0527 | 3.8181 | 3.8 | 431 | 17.9583
| 432 | 3.8181 | 718.1367 | 3.7623 | 3.8 | 432 | 18
| 433 | 3.7623 | 717.2218 | 3.7065 | 3.7 | 433 | 18.0417
| 434 | 3.7065 | 716.3081 | 3.6509 | 3.7 | 434 | 18.0833
| 435 | 3.6509 | 715.3956 | 3.5952 | 3.6 | 435 | 18.125 | 416887.1646
| 436 | 3.5952 | 714.4843 | 3.5397 | 3.5 | 436 | 18.1667
| 437 | 3.5397 | 713.5741 | 3.4842 | 3.5 | 437 | 18.2083
| 438 | 3.4842 | 712.665 | 3.4288 | 3.4 | 438 | 18.25
| 439 | 3.4288 | 711.7571 | 3.3735 | 3.4 | 439 | 18.2917
| 440 | 3.3735 | 710.8504 | 3.3183 | 3.3 | 440 | 18.3333
| 441 | 3.3183 | 709.9448 | 3.2631 | 3.3 | 441 | 18.375
| 442 | 3.2631 | 709.0404 | 3.208 | 3.2 | 442 | 18.4167
| 443 | 3.208 | 708.1372 | 3.1529 | 3.2 | 443 | 18.4583
| 444 | 3.1529 | 707.235 | 3.098 | 3.1 | 444 | 18.5
| 445 | 3.098 | 706.3341 | 3.043 | 3 | 445 | 18.5417
| 446 | 3.043 | 705.4343 | 2.9882 | 3 | 446 | 18.5833
| 447 | 2.9882 | 704.5356 | 2.9335 | 2.9 | 447 | 18.625
| 448 | 2.9335 | 703.6381 | 2.8788 | 2.9 | 448 | 18.6667
| 449 | 2.8788 | 702.7417 | 2.8241 | 2.8 | 449 | 18.7083
| 450 | 2.8241 | 701.8464 | 2.7696 | 2.8 | 450 | 18.75
| 451 | 2.7696 | 700.9524 | 2.7151 | 2.7 | 451 | 18.7917
| 452 | 2.7151 | 700.0594 | 2.6607 | 2.7 | 452 | 18.8333
| 453 | 2.6607 | 699.1676 | 2.6063 | 2.6 | 453 | 18.875
| 454 | 2.6063 | 698.2769 | 2.5521 | 2.6 | 454 | 18.9167
| 455 | 2.5521 | 697.3873 | 2.4978 | 2.5 | 455 | 18.9583
| 456 | 2.4978 | 696.4989 | 2.4437 | 2.4 | 456 | 19
| 457 | 2.4437 | 695.6116 | 2.3896 | 2.4 | 457 | 19.0417
| 458 | 2.3896 | 694.7255 | 2.3356 | 2.3 | 458 | 19.0833
| 459 | 2.3356 | 693.8404 | 2.2817 | 2.3 | 459 | 19.125
| 460 | 2.2817 | 692.9565 | 2.2278 | 2.2 | 460 | 19.1667
| 461 | 2.2278 | 692.0738 | 2.174 | 2.2 | 461 | 19.2083
| 462 | 2.174 | 691.1921 | 2.1203 | 2.1 | 462 | 19.25
| 463 | 2.1203 | 690.3116 | 2.0667 | 2.1 | 463 | 19.2917
| 464 | 2.0667 | 689.4322 | 2.0131 | 2 | 464 | 19.3333
| 465 | 2.0131 | 688.5539 | 1.9595 | 2 | 465 | 19.375
| 466 | 1.9595 | 687.6767 | 1.9061 | 1.9 | 466 | 19.4167
| 467 | 1.9061 | 686.8007 | 1.8527 | 1.9 | 467 | 19.4583
| 468 | 1.8527 | 685.9257 | 1.7994 | 1.8 | 468 | 19.5
| 469 | 1.7994 | 685.0519 | 1.7461 | 1.7 | 469 | 19.5417
| 470 | 1.7461 | 684.1792 | 1.693 | 1.7 | 470 | 19.5833
| 471 | 1.693 | 683.3076 | 1.6398 | 1.6 | 471 | 19.625
| 472 | 1.6398 | 682.4372 | 1.5868 | 1.6 | 472 | 19.6667
| 473 | 1.5868 | 681.5678 | 1.5338 | 1.5 | 473 | 19.7083
| 474 | 1.5338 | 680.6995 | 1.4809 | 1.5 | 474 | 19.75
| 475 | 1.4809 | 679.8324 | 1.4281 | 1.4 | 475 | 19.7917
| 476 | 1.4281 | 678.9663 | 1.3753 | 1.4 | 476 | 19.8333
| 477 | 1.3753 | 678.1013 | 1.3226 | 1.3 | 477 | 19.875
| 478 | 1.3226 | 677.2375 | 1.2699 | 1.3 | 478 | 19.9167
| 479 | 1.2699 | 676.3747 | 1.2174 | 1.2 | 479 | 19.9583
| 480 | 1.2174 | 675.5131 | 1.1649 | 1.2 | 480 | 20
| 481 | 1.1649 | 674.6525 | 1.1124 | 1.1 | 481 | 20.0417
| 482 | 1.1124 | 673.7931 | 1.06 | 1.1 | 482 | 20.0833
| 483 | 1.06 | 672.9347 | 1.0077 | 1 | 483 | 20.125
| 484 | 1.0077 | 672.0775 | 0.9555 | 1 | 484 | 20.1667
| 485 | 0.9555 | 671.2213 | 0.90332 | 0.9 | 485 | 20.2083
| 486 | 0.90332 | 670.3662 | 0.85121 | 0.9 | 486 | 20.25
| 487 | 0.85121 | 669.5122 | 0.79917 | 0.8 | 487 | 20.2917
| 488 | 0.79917 | 668.6593 | 0.7472 | 0.7 | 488 | 20.3333
| 489 | 0.7472 | 667.8075 | 0.69529 | 0.7 | 489 | 20.375
| 490 | 0.69529 | 666.9567 | 0.64345 | 0.6 | 490 | 20.4167
| 491 | 0.64345 | 666.1071 | 0.59167 | 0.6 | 491 | 20.4583
| 492 | 0.59167 | 665.2585 | 0.53996 | 0.5 | 492 | 20.5
| 493 | 0.53996 | 664.411 | 0.48831 | 0.5 | 493 | 20.5417
| 494 | 0.48831 | 663.5646 | 0.43673 | 0.4 | 494 | 20.5833
| 495 | 0.43673 | 662.7193 | 0.38522 | 0.4 | 495 | 20.625
| 496 | 0.38522 | 661.875 | 0.33377 | 0.3 | 496 | 20.6667
| 497 | 0.33377 | 661.0318 | 0.28239 | 0.3 | 497 | 20.7083
| 498 | 0.28239 | 660.1897 | 0.23107 | 0.2 | 498 | 20.75
| 499 | 0.23107 | 659.3487 | 0.17982 | 0.2 | 499 | 20.7917
| 500 | 0.17982 | 658.5087 | 0.12864 | 0.1 | 500 | 20.8333
| 501 | 0.12864 | 657.6699 | 0.077516 | 0.1 | 501 | 20.875
| 502 | 0.077516 | 656.832 | 0.02646 | 0 | 502 | 20.9167
| 503 | 0.02646 | 655.9953 | -0.024531 | 0 | 503 | 20.9583
| 504 | -0.024531 | 655.1596 | -0.075456 | -0.1 | 504 | 21
| 505 | -0.075456 | 654.325 | -0.12632 | -0.1 | 505 | 21.0417
| 506 | -0.12632 | 653.4914 | -0.17711 | -0.2 | 506 | 21.0833
| 507 | -0.17711 | 652.6589 | -0.22784 | -0.2 | 507 | 21.125
| 508 | -0.22784 | 651.8275 | -0.27851 | -0.3 | 508 | 21.1667
| 509 | -0.27851 | 650.9971 | -0.32911 | -0.3 | 509 | 21.2083
| 510 | -0.32911 | 650.1678 | -0.37965 | -0.4 | 510 | 21.25
| 511 | -0.37965 | 649.3395 | -0.43012 | -0.4 | 511 | 21.2917
| 512 | -0.43012 | 648.5123 | -0.48053 | -0.5 | 512 | 21.3333
| 513 | -0.48053 | 647.6861 | -0.53088 | -0.5 | 513 | 21.375
| 514 | -0.53088 | 646.861 | -0.58116 | -0.6 | 514 | 21.4167
| 515 | -0.58116 | 646.037 | -0.63138 | -0.6 | 515 | 21.4583
| 516 | -0.63138 | 645.214 | -0.68153 | -0.7 | 516 | 21.5
| 517 | -0.68153 | 644.392 | -0.73162 | -0.7 | 517 | 21.5417
| 518 | -0.73162 | 643.5711 | -0.78164 | -0.8 | 518 | 21.5833
| 519 | -0.78164 | 642.7513 | -0.8316 | -0.8 | 519 | 21.625
| 520 | -0.8316 | 641.9324 | -0.8815 | -0.9 | 520 | 21.6667
| 521 | -0.8815 | 641.1147 | -0.93134 | -0.9 | 521 | 21.7083
| 522 | -0.93134 | 640.2979 | -0.98111 | -1 | 522 | 21.75
| 523 | -0.98111 | 639.4822 | -1.0308 | -1 | 523 | 21.7917
| 524 | -1.0308 | 638.6676 | -1.0805 | -1.1 | 524 | 21.8333
| 525 | -1.0805 | 637.854 | -1.13 | -1.1 | 525 | 21.875
| 526 | -1.13 | 637.0414 | -1.1796 | -1.2 | 526 | 21.9167
| 527 | -1.1796 | 636.2299 | -1.229 | -1.2 | 527 | 21.9583
| 528 | -1.229 | 635.4194 | -1.2784 | -1.3 | 528 | 22
| 529 | -1.2784 | 634.6099 | -1.3277 | -1.3 | 529 | 22.0417
| 530 | -1.3277 | 633.8014 | -1.377 | -1.4 | 530 | 22.0833
| 531 | -1.377 | 632.994 | -1.4262 | -1.4 | 531 | 22.125
| 532 | -1.4262 | 632.1876 | -1.4753 | -1.5 | 532 | 22.1667
| 533 | -1.4753 | 631.3823 | -1.5244 | -1.5 | 533 | 22.2083
| 534 | -1.5244 | 630.5779 | -1.5734 | -1.6 | 534 | 22.25
| 535 | -1.5734 | 629.7746 | -1.6224 | -1.6 | 535 | 22.2917
| 536 | -1.6224 | 628.9723 | -1.6713 | -1.7 | 536 | 22.3333
| 537 | -1.6713 | 628.1711 | -1.7201 | -1.7 | 537 | 22.375
| 538 | -1.7201 | 627.3708 | -1.7689 | -1.8 | 538 | 22.4167
| 539 | -1.7689 | 626.5716 | -1.8176 | -1.8 | 539 | 22.4583
| 540 | -1.8176 | 625.7734 | -1.8662 | -1.9 | 540 | 22.5
| 541 | -1.8662 | 624.9762 | -1.9148 | -1.9 | 541 | 22.5417
| 542 | -1.9148 | 624.18 | -1.9633 | -2 | 542 | 22.5833
| 543 | -1.9633 | 623.3849 | -2.0118 | -2 | 543 | 22.625
| 544 | -2.0118 | 622.5907 | -2.0602 | -2.1 | 544 | 22.6667
| 545 | -2.0602 | 621.7976 | -2.1085 | -2.1 | 545 | 22.7083
| 546 | -2.1085 | 621.0055 | -2.1568 | -2.2 | 546 | 22.75
| 547 | -2.1568 | 620.2144 | -2.205 | -2.2 | 547 | 22.7917
| 548 | -2.205 | 619.4243 | -2.2531 | -2.3 | 548 | 22.8333
| 549 | -2.2531 | 618.6352 | -2.3012 | -2.3 | 549 | 22.875
| 550 | -2.3012 | 617.8471 | -2.3492 | -2.3 | 550 | 22.9167
| 551 | -2.3492 | 617.06 | -2.3972 | -2.4 | 551 | 22.9583
| 552 | -2.3972 | 616.2739 | -2.4451 | -2.4 | 552 | 23
| 553 | -2.4451 | 615.4888 | -2.4929 | -2.5 | 553 | 23.0417
| 554 | -2.4929 | 614.7047 | -2.5407 | -2.5 | 554 | 23.0833
| 555 | -2.5407 | 613.9216 | -2.5884 | -2.6 | 555 | 23.125
| 556 | -2.5884 | 613.1395 | -2.6361 | -2.6 | 556 | 23.1667
| 557 | -2.6361 | 612.3584 | -2.6837 | -2.7 | 557 | 23.2083
| 558 | -2.6837 | 611.5784 | -2.7312 | -2.7 | 558 | 23.25
| 559 | -2.7312 | 610.7992 | -2.7787 | -2.8 | 559 | 23.2917
| 560 | -2.7787 | 610.0211 | -2.8261 | -2.8 | 560 | 23.3333
| 561 | -2.8261 | 609.244 | -2.8735 | -2.9 | 561 | 23.375
| 562 | -2.8735 | 608.4679 | -2.9208 | -2.9 | 562 | 23.4167
| 563 | -2.9208 | 607.6927 | -2.968 | -3 | 563 | 23.4583
| 564 | -2.968 | 606.9186 | -3.0152 | -3 | 564 | 23.5
| 565 | -3.0152 | 606.1454 | -3.0623 | -3.1 | 565 | 23.5417
| 566 | -3.0623 | 605.3732 | -3.1094 | -3.1 | 566 | 23.5833
| 567 | -3.1094 | 604.602 | -3.1564 | -3.2 | 567 | 23.625
| 568 | -3.1564 | 603.8318 | -3.2033 | -3.2 | 568 | 23.6667
| 569 | -3.2033 | 603.0626 | -3.2502 | -3.3 | 569 | 23.7083
| 570 | -3.2502 | 602.2943 | -3.297 | -3.3 | 570 | 23.75
| 571 | -3.297 | 601.527 | -3.3438 | -3.3 | 571 | 23.7917
| 572 | -3.3438 | 600.7607 | -3.3904 | -3.4 | 572 | 23.8333
| 573 | -3.3904 | 599.9954 | -3.4371 | -3.4 | 573 | 23.875
| 574 | -3.4371 | 599.2311 | -3.4837 | -3.5 | 574 | 23.9167
| 575 | -3.4837 | 598.4677 | -3.5302 | -3.5 | 575 | 23.9583
| 576 | -3.5302 | 597.7053 | -3.5766 | -3.6 | 576 | 24
| 577 | -3.5766 | 596.9439 | -3.623 | -3.6 | 577 | 24.0417
| 578 | -3.623 | 596.1834 | -3.6694 | -3.7 | 578 | 24.0833
| 579 | -3.6694 | 595.4239 | -3.7157 | -3.7 | 579 | 24.125
| 580 | -3.7157 | 594.6654 | -3.7619 | -3.8 | 580 | 24.1667
| 581 | -3.7619 | 593.9078 | -3.8081 | -3.8 | 581 | 24.2083
| 582 | -3.8081 | 593.1512 | -3.8542 | -3.9 | 582 | 24.25
| 583 | -3.8542 | 592.3956 | -3.9002 | -3.9 | 583 | 24.2917
| 584 | -3.9002 | 591.6409 | -3.9462 | -3.9 | 584 | 24.3333
| 585 | -3.9462 | 590.8872 | -3.9921 | -4 | 585 | 24.375
| 586 | -3.9921 | 590.1345 | -4.038 | -4 | 586 | 24.4167
| 587 | -4.038 | 589.3827 | -4.0838 | -4.1 | 587 | 24.4583
| 588 | -4.0838 | 588.6319 | -4.1296 | -4.1 | 588 | 24.5
| 589 | -4.1296 | 587.882 | -4.1753 | -4.2 | 589 | 24.5417
| 590 | -4.1753 | 587.1331 | -4.2209 | -4.2 | 590 | 24.5833
| 591 | -4.2209 | 586.3851 | -4.2665 | -4.3 | 591 | 24.625
| 592 | -4.2665 | 585.6381 | -4.312 | -4.3 | 592 | 24.6667
| 593 | -4.312 | 584.892 | -4.3575 | -4.4 | 593 | 24.7083
| 594 | -4.3575 | 584.1469 | -4.4029 | -4.4 | 594 | 24.75
| 595 | -4.4029 | 583.4028 | -4.4482 | -4.4 | 595 | 24.7917
| 596 | -4.4482 | 582.6596 | -4.4935 | -4.5 | 596 | 24.8333
| 597 | -4.4935 | 581.9173 | -4.5387 | -4.5 | 597 | 24.875
| 598 | -4.5387 | 581.176 | -4.5839 | -4.6 | 598 | 24.9167
| 599 | -4.5839 | 580.4356 | -4.629 | -4.6 | 599 | 24.9583
| 600 | -4.629 | 579.6962 | -4.6741 | -4.7 | 600 | 25
| 601 | -4.6741 | 578.9577 | -4.7191 | -4.7 | 601 | 25.0417
| 602 | -4.7191 | 578.2201 | -4.764 | -4.8 | 602 | 25.0833
| 603 | -4.764 | 577.4835 | -4.8089 | -4.8 | 603 | 25.125
| 604 | -4.8089 | 576.7479 | -4.8538 | -4.9 | 604 | 25.1667
| 605 | -4.8538 | 576.0131 | -4.8985 | -4.9 | 605 | 25.2083
| 606 | -4.8985 | 575.2793 | -4.9433 | -4.9 | 606 | 25.25
| 607 | -4.9433 | 574.5465 | -4.9879 | -5 | 607 | 25.2917
| 608 | -4.9879 | 573.8145 | -5.0325 | -5 | 608 | 25.3333
| 609 | -5.0325 | 573.0835 | -5.0771 | -5.1 | 609 | 25.375
| 610 | -5.0771 | 572.3535 | -5.1215 | -5.1 | 610 | 25.4167
| 611 | -5.1215 | 571.6243 | -5.166 | -5.2 | 611 | 25.4583
| 612 | -5.166 | 570.8961 | -5.2104 | -5.2 | 612 | 25.5
| 613 | -5.2104 | 570.1689 | -5.2547 | -5.3 | 613 | 25.5417
| 614 | -5.2547 | 569.4425 | -5.2989 | -5.3 | 614 | 25.5833
| 615 | -5.2989 | 568.7171 | -5.3431 | -5.3 | 615 | 25.625
| 616 | -5.3431 | 567.9926 | -5.3873 | -5.4 | 616 | 25.6667
| 617 | -5.3873 | 567.269 | -5.4314 | -5.4 | 617 | 25.7083
| 618 | -5.4314 | 566.5463 | -5.4754 | -5.5 | 618 | 25.75
| 619 | -5.4754 | 565.8246 | -5.5194 | -5.5 | 619 | 25.7917
| 620 | -5.5194 | 565.1038 | -5.5633 | -5.6 | 620 | 25.8333
| 621 | -5.5633 | 564.3839 | -5.6072 | -5.6 | 621 | 25.875
| 622 | -5.6072 | 563.6649 | -5.651 | -5.7 | 622 | 25.9167
| 623 | -5.651 | 562.9468 | -5.6948 | -5.7 | 623 | 25.9583
| 624 | -5.6948 | 562.2297 | -5.7385 | -5.7 | 624 | 26
| 625 | -5.7385 | 561.5134 | -5.7821 | -5.8 | 625 | 26.0417
| 626 | -5.7821 | 560.7981 | -5.8257 | -5.8 | 626 | 26.0833
| 627 | -5.8257 | 560.0837 | -5.8693 | -5.9 | 627 | 26.125
| 628 | -5.8693 | 559.3702 | -5.9127 | -5.9 | 628 | 26.1667
| 629 | -5.9127 | 558.6576 | -5.9562 | -6 | 629 | 26.2083
| 630 | -5.9562 | 557.9459 | -5.9995 | -6 | 630 | 26.25
| 631 | -5.9995 | 557.2351 | -6.0428 | -6 | 631 | 26.2917
| 632 | -6.0428 | 556.5253 | -6.0861 | -6.1 | 632 | 26.3333
| 633 | -6.0861 | 555.8163 | -6.1293 | -6.1 | 633 | 26.375
| 634 | -6.1293 | 555.1082 | -6.1725 | -6.2 | 634 | 26.4167
| 635 | -6.1725 | 554.401 | -6.2155 | -6.2 | 635 | 26.4583
| 636 | -6.2155 | 553.6948 | -6.2586 | -6.3 | 636 | 26.5
| 637 | -6.2586 | 552.9894 | -6.3016 | -6.3 | 637 | 26.5417
| 638 | -6.3016 | 552.285 | -6.3445 | -6.3 | 638 | 26.5833
| 639 | -6.3445 | 551.5814 | -6.3874 | -6.4 | 639 | 26.625
| 640 | -6.3874 | 550.8787 | -6.4302 | -6.4 | 640 | 26.6667
| 641 | -6.4302 | 550.1769 | -6.473 | -6.5 | 641 | 26.7083
| 642 | -6.473 | 549.476 | -6.5157 | -6.5 | 642 | 26.75
| 643 | -6.5157 | 548.7761 | -6.5583 | -6.6 | 643 | 26.7917
| 644 | -6.5583 | 548.077 | -6.6009 | -6.6 | 644 | 26.8333
| 645 | -6.6009 | 547.3787 | -6.6435 | -6.6 | 645 | 26.875
| 646 | -6.6435 | 546.6814 | -6.686 | -6.7 | 646 | 26.9167
| 647 | -6.686 | 545.985 | -6.7284 | -6.7 | 647 | 26.9583
| 648 | -6.7284 | 545.2895 | -6.7708 | -6.8 | 648 | 27
| 649 | -6.7708 | 544.5948 | -6.8131 | -6.8 | 649 | 27.0417
| 650 | -6.8131 | 543.901 | -6.8554 | -6.9 | 650 | 27.0833
| 651 | -6.8554 | 543.2081 | -6.8976 | -6.9 | 651 | 27.125
| 652 | -6.8976 | 542.5161 | -6.9398 | -6.9 | 652 | 27.1667
| 653 | -6.9398 | 541.825 | -6.9819 | -7 | 653 | 27.2083
| 654 | -6.9819 | 541.1348 | -7.024 | -7 | 654 | 27.25
| 655 | -7.024 | 540.4454 | -7.066 | -7.1 | 655 | 27.2917
| 656 | -7.066 | 539.7569 | -7.1079 | -7.1 | 656 | 27.3333
| 657 | -7.1079 | 539.0693 | -7.1498 | -7.1 | 657 | 27.375
| 658 | -7.1498 | 538.3826 | -7.1917 | -7.2 | 658 | 27.4167
| 659 | -7.1917 | 537.6967 | -7.2335 | -7.2 | 659 | 27.4583
| 660 | -7.2335 | 537.0117 | -7.2752 | -7.3 | 660 | 27.5
| 661 | -7.2752 | 536.3276 | -7.3169 | -7.3 | 661 | 27.5417
| 662 | -7.3169 | 535.6444 | -7.3586 | -7.4 | 662 | 27.5833
| 663 | -7.3586 | 534.962 | -7.4001 | -7.4 | 663 | 27.625
| 664 | -7.4001 | 534.2805 | -7.4417 | -7.4 | 664 | 27.6667
| 665 | -7.4417 | 533.5999 | -7.4831 | -7.5 | 665 | 27.7083
| 666 | -7.4831 | 532.9201 | -7.5246 | -7.5 | 666 | 27.75
| 667 | -7.5246 | 532.2412 | -7.5659 | -7.6 | 667 | 27.7917
| 668 | -7.5659 | 531.5632 | -7.6073 | -7.6 | 668 | 27.8333
| 669 | -7.6073 | 530.886 | -7.6485 | -7.6 | 669 | 27.875
| 670 | -7.6485 | 530.2097 | -7.6897 | -7.7 | 670 | 27.9167
| 671 | -7.6897 | 529.5342 | -7.7309 | -7.7 | 671 | 27.9583
| 672 | -7.7309 | 528.8596 | -7.772 | -7.8 | 672 | 28
| 673 | -7.772 | 528.1859 | -7.8131 | -7.8 | 673 | 28.0417
| 674 | -7.8131 | 527.5131 | -7.8541 | -7.9 | 674 | 28.0833
| 675 | -7.8541 | 526.841 | -7.895 | -7.9 | 675 | 28.125
| 676 | -7.895 | 526.1699 | -7.9359 | -7.9 | 676 | 28.1667
| 677 | -7.9359 | 525.4996 | -7.9768 | -8 | 677 | 28.2083
| 678 | -7.9768 | 524.8301 | -8.0176 | -8 | 678 | 28.25
| 679 | -8.0176 | 524.1615 | -8.0583 | -8.1 | 679 | 28.2917
| 680 | -8.0583 | 523.4938 | -8.099 | -8.1 | 680 | 28.3333
| 681 | -8.099 | 522.8269 | -8.1396 | -8.1 | 681 | 28.375
| 682 | -8.1396 | 522.1609 | -8.1802 | -8.2 | 682 | 28.4167
| 683 | -8.1802 | 521.4957 | -8.2208 | -8.2 | 683 | 28.4583
| 684 | -8.2208 | 520.8313 | -8.2612 | -8.3 | 684 | 28.5
| 685 | -8.2612 | 520.1678 | -8.3017 | -8.3 | 685 | 28.5417
| 686 | -8.3017 | 519.5052 | -8.3421 | -8.3 | 686 | 28.5833
| 687 | -8.3421 | 518.8434 | -8.3824 | -8.4 | 687 | 28.625
| 688 | -8.3824 | 518.1824 | -8.4227 | -8.4 | 688 | 28.6667
| 689 | -8.4227 | 517.5223 | -8.4629 | -8.5 | 689 | 28.7083
| 690 | -8.4629 | 516.863 | -8.5031 | -8.5 | 690 | 28.75
| 691 | -8.5031 | 516.2045 | -8.5432 | -8.5 | 691 | 28.7917
| 692 | -8.5432 | 515.5469 | -8.5833 | -8.6 | 692 | 28.8333
| 693 | -8.5833 | 514.8902 | -8.6233 | -8.6 | 693 | 28.875
| 694 | -8.6233 | 514.2342 | -8.6633 | -8.7 | 694 | 28.9167
| 695 | -8.6633 | 513.5791 | -8.7032 | -8.7 | 695 | 28.9583
| 696 | -8.7032 | 512.9249 | -8.743 | -8.7 | 696 | 29
| 697 | -8.743 | 512.2715 | -8.7829 | -8.8 | 697 | 29.0417
| 698 | -8.7829 | 511.6189 | -8.8226 | -8.8 | 698 | 29.0833
| 699 | -8.8226 | 510.9671 | -8.8624 | -8.9 | 699 | 29.125
| 700 | -8.8624 | 510.3162 | -8.902 | -8.9 | 700 | 29.1667
| 701 | -8.902 | 509.6661 | -8.9416 | -8.9 | 701 | 29.2083
| 702 | -8.9416 | 509.0168 | -8.9812 | -9 | 702 | 29.25
| 703 | -8.9812 | 508.3683 | -9.0207 | -9 | 703 | 29.2917
| 704 | -9.0207 | 507.7207 | -9.0602 | -9.1 | 704 | 29.3333
| 705 | -9.0602 | 507.0739 | -9.0996 | -9.1 | 705 | 29.375
| 706 | -9.0996 | 506.4279 | -9.139 | -9.1 | 706 | 29.4167
| 707 | -9.139 | 505.7828 | -9.1783 | -9.2 | 707 | 29.4583
| 708 | -9.1783 | 505.1385 | -9.2175 | -9.2 | 708 | 29.5
| 709 | -9.2175 | 504.4949 | -9.2568 | -9.3 | 709 | 29.5417
| 710 | -9.2568 | 503.8523 | -9.2959 | -9.3 | 710 | 29.5833
| 711 | -9.2959 | 503.2104 | -9.335 | -9.3 | 711 | 29.625
| 712 | -9.335 | 502.5693 | -9.3741 | -9.4 | 712 | 29.6667
| 713 | -9.3741 | 501.9291 | -9.4131 | -9.4 | 713 | 29.7083
| 714 | -9.4131 | 501.2897 | -9.4521 | -9.5 | 714 | 29.75
| 715 | -9.4521 | 500.6511 | -9.491 | -9.5 | 715 | 29.7917
| 716 | -9.491 | 500.0133 | -9.5299 | -9.5 | 716 | 29.8333
| 717 | -9.5299 | 499.3763 | -9.5687 | -9.6 | 717 | 29.875
| 718 | -9.5687 | 498.7401 | -9.6074 | -9.6 | 718 | 29.9167
| 719 | -9.6074 | 498.1048 | -9.6462 | -9.6 | 719 | 29.9583
| 720 | -9.6462 | 497.4702 | -9.6848 | -9.7 | 720 | 30
| 721 | -9.6848 | 496.8365 | -9.7235 | -9.7 | 721 | 30.0417
| 722 | -9.7235 | 496.2036 | -9.762 | -9.8 | 722 | 30.0833
| 723 | -9.762 | 495.5714 | -9.8005 | -9.8 | 723 | 30.125
| 724 | -9.8005 | 494.9401 | -9.839 | -9.8 | 724 | 30.1667
| 725 | -9.839 | 494.3096 | -9.8774 | -9.9 | 725 | 30.2083
| 726 | -9.8774 | 493.6799 | -9.9158 | -9.9 | 726 | 30.25
| 727 | -9.9158 | 493.051 | -9.9541 | -10 | 727 | 30.2917
| 728 | -9.9541 | 492.4229 | -9.9924 | -10 | 728 | 30.3333
| 729 | -9.9924 | 491.7956 | -10.0306 | -10 | 729 | 30.375
| 730 | -10.0306 | 491.169 | -10.0688 | -10.1 | 730 | 30.4167
| 731 | -10.0688 | 490.5433 | -10.107 | -10.1 | 731 | 30.4583
| 732 | -10.107 | 489.9184 | -10.145 | -10.1 | 732 | 30.5
| 733 | -10.145 | 489.2943 | -10.1831 | -10.2 | 733 | 30.5417
| 734 | -10.1831 | 488.671 | -10.221 | -10.2 | 734 | 30.5833
| 735 | -10.221 | 488.0484 | -10.259 | -10.3 | 735 | 30.625
| 736 | -10.259 | 487.4267 | -10.2969 | -10.3 | 736 | 30.6667
| 737 | -10.2969 | 486.8058 | -10.3347 | -10.3 | 737 | 30.7083
| 738 | -10.3347 | 486.1856 | -10.3725 | -10.4 | 738 | 30.75
| 739 | -10.3725 | 485.5662 | -10.4102 | -10.4 | 739 | 30.7917
| 740 | -10.4102 | 484.9477 | -10.4479 | -10.4 | 740 | 30.8333
| 741 | -10.4479 | 484.3299 | -10.4856 | -10.5 | 741 | 30.875
| 742 | -10.4856 | 483.7129 | -10.5232 | -10.5 | 742 | 30.9167
| 743 | -10.5232 | 483.0967 | -10.5607 | -10.6 | 743 | 30.9583
| 744 | -10.5607 | 482.4812 | -10.5982 | -10.6 | 744 | 31
| 745 | -10.5982 | 481.8666 | -10.6357 | -10.6 | 745 | 31.0417
| 746 | -10.6357 | 481.2527 | -10.6731 | -10.7 | 746 | 31.0833
| 747 | -10.6731 | 480.6397 | -10.7105 | -10.7 | 747 | 31.125
| 748 | -10.7105 | 480.0274 | -10.7478 | -10.7 | 748 | 31.1667
| 749 | -10.7478 | 479.4158 | -10.785 | -10.8 | 749 | 31.2083
| 750 | -10.785 | 478.8051 | -10.8223 | -10.8 | 750 | 31.25
| 751 | -10.8223 | 478.1951 | -10.8594 | -10.9 | 751 | 31.2917
| 752 | -10.8594 | 477.5859 | -10.8966 | -10.9 | 752 | 31.3333
| 753 | -10.8966 | 476.9775 | -10.9336 | -10.9 | 753 | 31.375
| 754 | -10.9336 | 476.3699 | -10.9707 | -11 | 754 | 31.4167
| 755 | -10.9707 | 475.763 | -11.0076 | -11 | 755 | 31.4583
| 756 | -11.0076 | 475.157 | -11.0446 | -11 | 756 | 31.5
| 757 | -11.0446 | 474.5516 | -11.0815 | -11.1 | 757 | 31.5417
| 758 | -11.0815 | 473.9471 | -11.1183 | -11.1 | 758 | 31.5833
| 759 | -11.1183 | 473.3433 | -11.1551 | -11.2 | 759 | 31.625
| 760 | -11.1551 | 472.7403 | -11.1918 | -11.2 | 760 | 31.6667
| 761 | -11.1918 | 472.1381 | -11.2285 | -11.2 | 761 | 31.7083
| 762 | -11.2285 | 471.5366 | -11.2652 | -11.3 | 762 | 31.75
| 763 | -11.2652 | 470.9359 | -11.3018 | -11.3 | 763 | 31.7917
| 764 | -11.3018 | 470.336 | -11.3384 | -11.3 | 764 | 31.8333
| 765 | -11.3384 | 469.7368 | -11.3749 | -11.4 | 765 | 31.875
| 766 | -11.3749 | 469.1384 | -11.4113 | -11.4 | 766 | 31.9167
| 767 | -11.4113 | 468.5408 | -11.4478 | -11.4 | 767 | 31.9583
| 768 | -11.4478 | 467.9439 | -11.4841 | -11.5 | 768 | 32
| 769 | -11.4841 | 467.3477 | -11.5205 | -11.5 | 769 | 32.0417
| 770 | -11.5205 | 466.7524 | -11.5567 | -11.6 | 770 | 32.0833
| 771 | -11.5567 | 466.1578 | -11.593 | -11.6 | 771 | 32.125
| 772 | -11.593 | 465.5639 | -11.6292 | -11.6 | 772 | 32.1667
| 773 | -11.6292 | 464.9708 | -11.6653 | -11.7 | 773 | 32.2083
| 774 | -11.6653 | 464.3785 | -11.7014 | -11.7 | 774 | 32.25
| 775 | -11.7014 | 463.7869 | -11.7375 | -11.7 | 775 | 32.2917
| 776 | -11.7375 | 463.1961 | -11.7735 | -11.8 | 776 | 32.3333
| 777 | -11.7735 | 462.606 | -11.8094 | -11.8 | 777 | 32.375
| 778 | -11.8094 | 462.0167 | -11.8453 | -11.8 | 778 | 32.4167
| 779 | -11.8453 | 461.4281 | -11.8812 | -11.9 | 779 | 32.4583
| 780 | -11.8812 | 460.8403 | -11.917 | -11.9 | 780 | 32.5
| 781 | -11.917 | 460.2532 | -11.9528 | -12 | 781 | 32.5417
| 782 | -11.9528 | 459.6669 | -11.9885 | -12 | 782 | 32.5833
| 783 | -11.9885 | 459.0813 | -12.0242 | -12 | 783 | 32.625
| 784 | -12.0242 | 458.4965 | -12.0598 | -12.1 | 784 | 32.6667
| 785 | -12.0598 | 457.9124 | -12.0954 | -12.1 | 785 | 32.7083
| 786 | -12.0954 | 457.329 | -12.131 | -12.1 | 786 | 32.75
| 787 | -12.131 | 456.7464 | -12.1665 | -12.2 | 787 | 32.7917
| 788 | -12.1665 | 456.1646 | -12.2019 | -12.2 | 788 | 32.8333
| 789 | -12.2019 | 455.5834 | -12.2374 | -12.2 | 789 | 32.875
| 790 | -12.2374 | 455.0031 | -12.2727 | -12.3 | 790 | 32.9167
| 791 | -12.2727 | 454.4234 | -12.308 | -12.3 | 791 | 32.9583
| 792 | -12.308 | 453.8445 | -12.3433 | -12.3 | 792 | 33
| 793 | -12.3433 | 453.2664 | -12.3786 | -12.4 | 793 | 33.0417
| 794 | -12.3786 | 452.6889 | -12.4137 | -12.4 | 794 | 33.0833
| 795 | -12.4137 | 452.1122 | -12.4489 | -12.4 | 795 | 33.125
| 796 | -12.4489 | 451.5363 | -12.484 | -12.5 | 796 | 33.1667
| 797 | -12.484 | 450.9611 | -12.519 | -12.5 | 797 | 33.2083
| 798 | -12.519 | 450.3866 | -12.554 | -12.6 | 798 | 33.25
| 799 | -12.554 | 449.8128 | -12.589 | -12.6 | 799 | 33.2917
| 800 | -12.589 | 449.2398 | -12.6239 | -12.6 | 800 | 33.3333
| 801 | -12.6239 | 448.6675 | -12.6588 | -12.7 | 801 | 33.375
| 802 | -12.6588 | 448.0959 | -12.6936 | -12.7 | 802 | 33.4167
| 803 | -12.6936 | 447.5251 | -12.7284 | -12.7 | 803 | 33.4583
| 804 | -12.7284 | 446.955 | -12.7632 | -12.8 | 804 | 33.5
| 805 | -12.7632 | 446.3856 | -12.7979 | -12.8 | 805 | 33.5417
| 806 | -12.7979 | 445.8169 | -12.8325 | -12.8 | 806 | 33.5833
| 807 | -12.8325 | 445.249 | -12.8671 | -12.9 | 807 | 33.625
| 808 | -12.8671 | 444.6818 | -12.9017 | -12.9 | 808 | 33.6667
| 809 | -12.9017 | 444.1153 | -12.9362 | -12.9 | 809 | 33.7083
| 810 | -12.9362 | 443.5495 | -12.9707 | -13 | 810 | 33.75
| 811 | -12.9707 | 442.9844 | -13.0051 | -13 | 811 | 33.7917
| 812 | -13.0051 | 442.4201 | -13.0395 | -13 | 812 | 33.8333
| 813 | -13.0395 | 441.8565 | -13.0739 | -13.1 | 813 | 33.875
| 814 | -13.0739 | 441.2936 | -13.1082 | -13.1 | 814 | 33.9167
| 815 | -13.1082 | 440.7314 | -13.1424 | -13.1 | 815 | 33.9583
| 816 | -13.1424 | 440.17 | -13.1766 | -13.2 | 816 | 34
| 817 | -13.1766 | 439.6092 | -13.2108 | -13.2 | 817 | 34.0417
| 818 | -13.2108 | 439.0492 | -13.2449 | -13.2 | 818 | 34.0833
| 819 | -13.2449 | 438.4899 | -13.279 | -13.3 | 819 | 34.125
| 820 | -13.279 | 437.9313 | -13.3131 | -13.3 | 820 | 34.1667
| 821 | -13.3131 | 437.3734 | -13.3471 | -13.3 | 821 | 34.2083
| 822 | -13.3471 | 436.8162 | -13.381 | -13.4 | 822 | 34.25
| 823 | -13.381 | 436.2598 | -13.4149 | -13.4 | 823 | 34.2917
| 824 | -13.4149 | 435.704 | -13.4488 | -13.4 | 824 | 34.3333
| 825 | -13.4488 | 435.1489 | -13.4826 | -13.5 | 825 | 34.375
| 826 | -13.4826 | 434.5946 | -13.5164 | -13.5 | 826 | 34.4167
| 827 | -13.5164 | 434.0409 | -13.5501 | -13.6 | 827 | 34.4583
| 828 | -13.5501 | 433.488 | -13.5838 | -13.6 | 828 | 34.5
| 829 | -13.5838 | 432.9358 | -13.6175 | -13.6 | 829 | 34.5417
| 830 | -13.6175 | 432.3843 | -13.6511 | -13.7 | 830 | 34.5833
| 831 | -13.6511 | 431.8334 | -13.6847 | -13.7 | 831 | 34.625
| 832 | -13.6847 | 431.2833 | -13.7182 | -13.7 | 832 | 34.6667
| 833 | -13.7182 | 430.7339 | -13.7517 | -13.8 | 833 | 34.7083
| 834 | -13.7517 | 430.1852 | -13.7851 | -13.8 | 834 | 34.75
| 835 | -13.7851 | 429.6371 | -13.8185 | -13.8 | 835 | 34.7917
| 836 | -13.8185 | 429.0898 | -13.8518 | -13.9 | 836 | 34.8333
| 837 | -13.8518 | 428.5432 | -13.8852 | -13.9 | 837 | 34.875
| 838 | -13.8852 | 427.9973 | -13.9184 | -13.9 | 838 | 34.9167
| 839 | -13.9184 | 427.452 | -13.9516 | -14 | 839 | 34.9583
| 840 | -13.9516 | 426.9075 | -13.9848 | -14 | 840 | 35
| 841 | -13.9848 | 426.3636 | -14.018 | -14 | 841 | 35.0417
| 842 | -14.018 | 425.8205 | -14.0511 | -14.1 | 842 | 35.0833
| 843 | -14.0511 | 425.278 | -14.0841 | -14.1 | 843 | 35.125
| 844 | -14.0841 | 424.7362 | -14.1171 | -14.1 | 844 | 35.1667
| 845 | -14.1171 | 424.1952 | -14.1501 | -14.2 | 845 | 35.2083
| 846 | -14.1501 | 423.6548 | -14.183 | -14.2 | 846 | 35.25
| 847 | -14.183 | 423.1151 | -14.2159 | -14.2 | 847 | 35.2917
| 848 | -14.2159 | 422.576 | -14.2488 | -14.2 | 848 | 35.3333
| 849 | -14.2488 | 422.0377 | -14.2816 | -14.3 | 849 | 35.375
| 850 | -14.2816 | 421.5001 | -14.3144 | -14.3 | 850 | 35.4167
| 851 | -14.3144 | 420.9631 | -14.3471 | -14.3 | 851 | 35.4583
| 852 | -14.3471 | 420.4268 | -14.3798 | -14.4 | 852 | 35.5
| 853 | -14.3798 | 419.8912 | -14.4124 | -14.4 | 853 | 35.5417
| 854 | -14.4124 | 419.3563 | -14.445 | -14.4 | 854 | 35.5833
| 855 | -14.445 | 418.8221 | -14.4775 | -14.5 | 855 | 35.625
| 856 | -14.4775 | 418.2886 | -14.5101 | -14.5 | 856 | 35.6667
| 857 | -14.5101 | 417.7557 | -14.5425 | -14.5 | 857 | 35.7083
| 858 | -14.5425 | 417.2235 | -14.575 | -14.6 | 858 | 35.75
| 859 | -14.575 | 416.692 | -14.6074 | -14.6 | 859 | 35.7917
| 860 | -14.6074 | 416.1611 | -14.6397 | -14.6 | 860 | 35.8333
| 861 | -14.6397 | 415.631 | -14.672 | -14.7 | 861 | 35.875
| 862 | -14.672 | 415.1015 | -14.7043 | -14.7 | 862 | 35.9167
| 863 | -14.7043 | 414.5727 | -14.7365 | -14.7 | 863 | 35.9583
| 864 | -14.7365 | 414.0446 | -14.7687 | -14.8 | 864 | 36
| 865 | -14.7687 | 413.5171 | -14.8008 | -14.8 | 865 | 36.0417
| 866 | -14.8008 | 412.9903 | -14.8329 | -14.8 | 866 | 36.0833
| 867 | -14.8329 | 412.4642 | -14.865 | -14.9 | 867 | 36.125
| 868 | -14.865 | 411.9387 | -14.897 | -14.9 | 868 | 36.1667
| 869 | -14.897 | 411.414 | -14.929 | -14.9 | 869 | 36.2083
| 870 | -14.929 | 410.8899 | -14.9609 | -15 | 870 | 36.25
| 871 | -14.9609 | 410.3664 | -14.9928 | -15 | 871 | 36.2917
| 872 | -14.9928 | 409.8436 | -15.0247 | -15 | 872 | 36.3333
| 873 | -15.0247 | 409.3215 | -15.0565 | -15.1 | 873 | 36.375
| 874 | -15.0565 | 408.8001 | -15.0883 | -15.1 | 874 | 36.4167
| 875 | -15.0883 | 408.2793 | -15.12 | -15.1 | 875 | 36.4583
| 876 | -15.12 | 407.7592 | -15.1517 | -15.2 | 876 | 36.5
| 877 | -15.1517 | 407.2397 | -15.1834 | -15.2 | 877 | 36.5417
| 878 | -15.1834 | 406.7209 | -15.215 | -15.2 | 878 | 36.5833
| 879 | -15.215 | 406.2028 | -15.2465 | -15.2 | 879 | 36.625
| 880 | -15.2465 | 405.6853 | -15.2781 | -15.3 | 880 | 36.6667
| 881 | -15.2781 | 405.1685 | -15.3096 | -15.3 | 881 | 36.7083
| 882 | -15.3096 | 404.6524 | -15.341 | -15.3 | 882 | 36.75
| 883 | -15.341 | 404.1369 | -15.3724 | -15.4 | 883 | 36.7917
| 884 | -15.3724 | 403.622 | -15.4038 | -15.4 | 884 | 36.8333
| 885 | -15.4038 | 403.1079 | -15.4352 | -15.4 | 885 | 36.875
| 886 | -15.4352 | 402.5943 | -15.4664 | -15.5 | 886 | 36.9167
| 887 | -15.4664 | 402.0814 | -15.4977 | -15.5 | 887 | 36.9583
| 888 | -15.4977 | 401.5692 | -15.5289 | -15.5 | 888 | 37
| 889 | -15.5289 | 401.0577 | -15.5601 | -15.6 | 889 | 37.0417
| 890 | -15.5601 | 400.5467 | -15.5912 | -15.6 | 890 | 37.0833
| 891 | -15.5912 | 400.0365 | -15.6223 | -15.6 | 891 | 37.125
| 892 | -15.6223 | 399.5269 | -15.6534 | -15.7 | 892 | 37.1667
| 893 | -15.6534 | 399.0179 | -15.6844 | -15.7 | 893 | 37.2083
| 894 | -15.6844 | 398.5096 | -15.7154 | -15.7 | 894 | 37.25
| 895 | -15.7154 | 398.0019 | -15.7463 | -15.7 | 895 | 37.2917
| 896 | -15.7463 | 397.4949 | -15.7772 | -15.8 | 896 | 37.3333
| 897 | -15.7772 | 396.9885 | -15.8081 | -15.8 | 897 | 37.375
| 898 | -15.8081 | 396.4828 | -15.8389 | -15.8 | 898 | 37.4167
| 899 | -15.8389 | 395.9777 | -15.8697 | -15.9 | 899 | 37.4583
| 900 | -15.8697 | 395.4732 | -15.9004 | -15.9 | 900 | 37.5
| 901 | -15.9004 | 394.9694 | -15.9311 | -15.9 | 901 | 37.5417
| 902 | -15.9311 | 394.4663 | -15.9618 | -16 | 902 | 37.5833
| 903 | -15.9618 | 393.9637 | -15.9924 | -16 | 903 | 37.625
| 904 | -15.9924 | 393.4619 | -16.023 | -16 | 904 | 37.6667
| 905 | -16.023 | 392.9606 | -16.0535 | -16.1 | 905 | 37.7083
| 906 | -16.0535 | 392.46 | -16.084 | -16.1 | 906 | 37.75
| 907 | -16.084 | 391.9601 | -16.1145 | -16.1 | 907 | 37.7917
| 908 | -16.1145 | 391.4607 | -16.1449 | -16.1 | 908 | 37.8333
| 909 | -16.1449 | 390.962 | -16.1753 | -16.2 | 909 | 37.875
| 910 | -16.1753 | 390.464 | -16.2057 | -16.2 | 910 | 37.9167
| 911 | -16.2057 | 389.9666 | -16.236 | -16.2 | 911 | 37.9583
| 912 | -16.236 | 389.4698 | -16.2662 | -16.3 | 912 | 38
| 913 | -16.2662 | 388.9736 | -16.2965 | -16.3 | 913 | 38.0417
| 914 | -16.2965 | 388.4781 | -16.3267 | -16.3 | 914 | 38.0833
| 915 | -16.3267 | 387.9832 | -16.3568 | -16.4 | 915 | 38.125
| 916 | -16.3568 | 387.4889 | -16.3869 | -16.4 | 916 | 38.1667
| 917 | -16.3869 | 386.9953 | -16.417 | -16.4 | 917 | 38.2083
| 918 | -16.417 | 386.5023 | -16.4471 | -16.4 | 918 | 38.25
| 919 | -16.4471 | 386.0099 | -16.4771 | -16.5 | 919 | 38.2917
| 920 | -16.4771 | 385.5182 | -16.507 | -16.5 | 920 | 38.3333
| 921 | -16.507 | 385.0271 | -16.537 | -16.5 | 921 | 38.375
| 922 | -16.537 | 384.5366 | -16.5669 | -16.6 | 922 | 38.4167
| 923 | -16.5669 | 384.0467 | -16.5967 | -16.6 | 923 | 38.4583
| 924 | -16.5967 | 383.5574 | -16.6265 | -16.6 | 924 | 38.5
| 925 | -16.6265 | 383.0688 | -16.6563 | -16.7 | 925 | 38.5417
| 926 | -16.6563 | 382.5808 | -16.686 | -16.7 | 926 | 38.5833
| 927 | -16.686 | 382.0934 | -16.7157 | -16.7 | 927 | 38.625
| 928 | -16.7157 | 381.6067 | -16.7454 | -16.7 | 928 | 38.6667
| 929 | -16.7454 | 381.1205 | -16.775 | -16.8 | 929 | 38.7083
| 930 | -16.775 | 380.635 | -16.8046 | -16.8 | 930 | 38.75
| 931 | -16.8046 | 380.1501 | -16.8342 | -16.8 | 931 | 38.7917
| 932 | -16.8342 | 379.6658 | -16.8637 | -16.9 | 932 | 38.8333
| 933 | -16.8637 | 379.1822 | -16.8931 | -16.9 | 933 | 38.875
| 934 | -16.8931 | 378.6991 | -16.9226 | -16.9 | 934 | 38.9167
| 935 | -16.9226 | 378.2167 | -16.952 | -17 | 935 | 38.9583
| 936 | -16.952 | 377.7349 | -16.9813 | -17 | 936 | 39
| 937 | -16.9813 | 377.2537 | -17.0107 | -17 | 937 | 39.0417
| 938 | -17.0107 | 376.7731 | -17.04 | -17 | 938 | 39.0833
| 939 | -17.04 | 376.2931 | -17.0692 | -17.1 | 939 | 39.125
| 940 | -17.0692 | 375.8137 | -17.0984 | -17.1 | 940 | 39.1667
| 941 | -17.0984 | 375.335 | -17.1276 | -17.1 | 941 | 39.2083
| 942 | -17.1276 | 374.8568 | -17.1567 | -17.2 | 942 | 39.25
| 943 | -17.1567 | 374.3793 | -17.1858 | -17.2 | 943 | 39.2917
| 944 | -17.1858 | 373.9024 | -17.2149 | -17.2 | 944 | 39.3333
| 945 | -17.2149 | 373.426 | -17.2439 | -17.2 | 945 | 39.375
| 946 | -17.2439 | 372.9503 | -17.2729 | -17.3 | 946 | 39.4167
| 947 | -17.2729 | 372.4752 | -17.3019 | -17.3 | 947 | 39.4583
| 948 | -17.3019 | 372.0007 | -17.3308 | -17.3 | 948 | 39.5
| 949 | -17.3308 | 371.5268 | -17.3597 | -17.4 | 949 | 39.5417
| 950 | -17.3597 | 371.0535 | -17.3885 | -17.4 | 950 | 39.5833
| 951 | -17.3885 | 370.5808 | -17.4173 | -17.4 | 951 | 39.625
| 952 | -17.4173 | 370.1087 | -17.4461 | -17.4 | 952 | 39.6667
| 953 | -17.4461 | 369.6372 | -17.4748 | -17.5 | 953 | 39.7083
| 954 | -17.4748 | 369.1663 | -17.5035 | -17.5 | 954 | 39.75
| 955 | -17.5035 | 368.696 | -17.5322 | -17.5 | 955 | 39.7917
| 956 | -17.5322 | 368.2264 | -17.5608 | -17.6 | 956 | 39.8333
| 957 | -17.5608 | 367.7573 | -17.5894 | -17.6 | 957 | 39.875
| 958 | -17.5894 | 367.2888 | -17.6179 | -17.6 | 958 | 39.9167
| 959 | -17.6179 | 366.8209 | -17.6464 | -17.6 | 959 | 39.9583
| 960 | -17.6464 | 366.3536 | -17.6749 | -17.7 | 960 | 40
| 961 | -17.6749 | 365.8869 | -17.7033 | -17.7 | 961 | 40.0417
| 962 | -17.7033 | 365.4207 | -17.7318 | -17.7 | 962 | 40.0833
| 963 | -17.7318 | 364.9552 | -17.7601 | -17.8 | 963 | 40.125
| 964 | -17.7601 | 364.4903 | -17.7885 | -17.8 | 964 | 40.1667
| 965 | -17.7885 | 364.026 | -17.8167 | -17.8 | 965 | 40.2083
| 966 | -17.8167 | 363.5622 | -17.845 | -17.8 | 966 | 40.25
| 967 | -17.845 | 363.0991 | -17.8732 | -17.9 | 967 | 40.2917
| 968 | -17.8732 | 362.6365 | -17.9014 | -17.9 | 968 | 40.3333
| 969 | -17.9014 | 362.1745 | -17.9296 | -17.9 | 969 | 40.375
| 970 | -17.9296 | 361.7132 | -17.9577 | -18 | 970 | 40.4167
| 971 | -17.9577 | 361.2524 | -17.9858 | -18 | 971 | 40.4583
| 972 | -17.9858 | 360.7922 | -18.0138 | -18 | 972 | 40.5
| 973 | -18.0138 | 360.3325 | -18.0418 | -18 | 973 | 40.5417
| 974 | -18.0418 | 359.8735 | -18.0698 | -18.1 | 974 | 40.5833
| 975 | -18.0698 | 359.415 | -18.0977 | -18.1 | 975 | 40.625
| 976 | -18.0977 | 358.9572 | -18.1256 | -18.1 | 976 | 40.6667
| 977 | -18.1256 | 358.4999 | -18.1535 | -18.2 | 977 | 40.7083
| 978 | -18.1535 | 358.0432 | -18.1813 | -18.2 | 978 | 40.75
| 979 | -18.1813 | 357.5871 | -18.2091 | -18.2 | 979 | 40.7917
| 980 | -18.2091 | 357.1315 | -18.2369 | -18.2 | 980 | 40.8333
| 981 | -18.2369 | 356.6766 | -18.2646 | -18.3 | 981 | 40.875
| 982 | -18.2646 | 356.2222 | -18.2923 | -18.3 | 982 | 40.9167
| 983 | -18.2923 | 355.7684 | -18.32 | -18.3 | 983 | 40.9583
| 984 | -18.32 | 355.3152 | -18.3476 | -18.3 | 984 | 41
| 985 | -18.3476 | 354.8625 | -18.3752 | -18.4 | 985 | 41.0417
| 986 | -18.3752 | 354.4105 | -18.4027 | -18.4 | 986 | 41.0833
| 987 | -18.4027 | 353.959 | -18.4302 | -18.4 | 987 | 41.125
| 988 | -18.4302 | 353.508 | -18.4577 | -18.5 | 988 | 41.1667
| 989 | -18.4577 | 353.0577 | -18.4851 | -18.5 | 989 | 41.2083
| 990 | -18.4851 | 352.6079 | -18.5125 | -18.5 | 990 | 41.25
| 991 | -18.5125 | 352.1587 | -18.5399 | -18.5 | 991 | 41.2917
| 992 | -18.5399 | 351.7101 | -18.5673 | -18.6 | 992 | 41.3333
| 993 | -18.5673 | 351.2621 | -18.5946 | -18.6 | 993 | 41.375
| 994 | -18.5946 | 350.8146 | -18.6218 | -18.6 | 994 | 41.4167
| 995 | -18.6218 | 350.3677 | -18.6491 | -18.6 | 995 | 41.4583
| 996 | -18.6491 | 349.9213 | -18.6763 | -18.7 | 996 | 41.5
| 997 | -18.6763 | 349.4756 | -18.7034 | -18.7 | 997 | 41.5417
| 998 | -18.7034 | 349.0304 | -18.7306 | -18.7 | 998 | 41.5833
| 999 | -18.7306 | 348.5857 | -18.7577 | -18.8 | 999 | 41.625
| 1000 | -18.7577 | 348.1416 | -18.7847 | -18.8 | 1000 | 41.6667
| 1001 | -18.7847 | 347.6981 | -18.8117 | -18.8 | 1001 | 41.7083
| 1002 | -18.8117 | 347.2552 | -18.8387 | -18.8 | 1002 | 41.75
| 1003 | -18.8387 | 346.8128 | -18.8657 | -18.9 | 1003 | 41.7917
| 1004 | -18.8657 | 346.371 | -18.8926 | -18.9 | 1004 | 41.8333
| 1005 | -18.8926 | 345.9298 | -18.9195 | -18.9 | 1005 | 41.875
| 1006 | -18.9195 | 345.4891 | -18.9464 | -18.9 | 1006 | 41.9167
| 1007 | -18.9464 | 345.0489 | -18.9732 | -19 | 1007 | 41.9583
| 1008 | -18.9732 | 344.6094 | -19 | -19 | 1008 | 42
| 1009 | -19 | 344.1704 | -19.0267 | -19 | 1009 | 42.0417
| 1010 | -19.0267 | 343.7319 | -19.0534 | -19.1 | 1010 | 42.0833
| 1011 | -19.0534 | 343.294 | -19.0801 | -19.1 | 1011 | 42.125
| 1012 | -19.0801 | 342.8567 | -19.1068 | -19.1 | 1012 | 42.1667
| 1013 | -19.1068 | 342.4199 | -19.1334 | -19.1 | 1013 | 42.2083
| 1014 | -19.1334 | 341.9837 | -19.16 | -19.2 | 1014 | 42.25
| 1015 | -19.16 | 341.548 | -19.1865 | -19.2 | 1015 | 42.2917
| 1016 | -19.1865 | 341.1129 | -19.213 | -19.2 | 1016 | 42.3333
| 1017 | -19.213 | 340.6784 | -19.2395 | -19.2 | 1017 | 42.375
| 1018 | -19.2395 | 340.2444 | -19.266 | -19.3 | 1018 | 42.4167
| 1019 | -19.266 | 339.8109 | -19.2924 | -19.3 | 1019 | 42.4583
| 1020 | -19.2924 | 339.378 | -19.3188 | -19.3 | 1020 | 42.5
| 1021 | -19.3188 | 338.9457 | -19.3451 | -19.3 | 1021 | 42.5417
| 1022 | -19.3451 | 338.5139 | -19.3714 | -19.4 | 1022 | 42.5833
| 1023 | -19.3714 | 338.0827 | -19.3977 | -19.4 | 1023 | 42.625
| 1024 | -19.3977 | 337.652 | -19.4239 | -19.4 | 1024 | 42.6667
| 1025 | -19.4239 | 337.2218 | -19.4502 | -19.5 | 1025 | 42.7083
| 1026 | -19.4502 | 336.7922 | -19.4763 | -19.5 | 1026 | 42.75
| 1027 | -19.4763 | 336.3632 | -19.5025 | -19.5 | 1027 | 42.7917
| 1028 | -19.5025 | 335.9347 | -19.5286 | -19.5 | 1028 | 42.8333
| 1029 | -19.5286 | 335.5067 | -19.5547 | -19.6 | 1029 | 42.875
| 1030 | -19.5547 | 335.0793 | -19.5807 | -19.6 | 1030 | 42.9167
| 1031 | -19.5807 | 334.6525 | -19.6067 | -19.6 | 1031 | 42.9583
| 1032 | -19.6067 | 334.2261 | -19.6327 | -19.6 | 1032 | 43
| 1033 | -19.6327 | 333.8004 | -19.6587 | -19.7 | 1033 | 43.0417
| 1034 | -19.6587 | 333.3751 | -19.6846 | -19.7 | 1034 | 43.0833
| 1035 | -19.6846 | 332.9504 | -19.7104 | -19.7 | 1035 | 43.125
| 1036 | -19.7104 | 332.5263 | -19.7363 | -19.7 | 1036 | 43.1667
| 1037 | -19.7363 | 332.1027 | -19.7621 | -19.8 | 1037 | 43.2083
| 1038 | -19.7621 | 331.6796 | -19.7879 | -19.8 | 1038 | 43.25
| 1039 | -19.7879 | 331.2571 | -19.8136 | -19.8 | 1039 | 43.2917
| 1040 | -19.8136 | 330.8351 | -19.8394 | -19.8 | 1040 | 43.3333
| 1041 | -19.8394 | 330.4136 | -19.865 | -19.9 | 1041 | 43.375
| 1042 | -19.865 | 329.9927 | -19.8907 | -19.9 | 1042 | 43.4167
| 1043 | -19.8907 | 329.5723 | -19.9163 | -19.9 | 1043 | 43.4583
| 1044 | -19.9163 | 329.1524 | -19.9419 | -19.9 | 1044 | 43.5
| 1045 | -19.9419 | 328.7331 | -19.9674 | -20 | 1045 | 43.5417
| 1046 | -19.9674 | 328.3143 | -19.993 | -20 | 1046 | 43.5833
| 1047 | -19.993 | 327.8961 | -20.0185 | -20 | 1047 | 43.625
| 1048 | -20.0185 | 327.4784 | -20.0439 | -20 | 1048 | 43.6667
| 1049 | -20.0439 | 327.0612 | -20.0693 | -20.1 | 1049 | 43.7083
| 1050 | -20.0693 | 326.6445 | -20.0947 | -20.1 | 1050 | 43.75
| 1051 | -20.0947 | 326.2284 | -20.1201 | -20.1 | 1051 | 43.7917
| 1052 | -20.1201 | 325.8128 | -20.1454 | -20.1 | 1052 | 43.8333
| 1053 | -20.1454 | 325.3978 | -20.1707 | -20.2 | 1053 | 43.875
| 1054 | -20.1707 | 324.9832 | -20.196 | -20.2 | 1054 | 43.9167
| 1055 | -20.196 | 324.5692 | -20.2212 | -20.2 | 1055 | 43.9583
| 1056 | -20.2212 | 324.1558 | -20.2464 | -20.2 | 1056 | 44
| 1057 | -20.2464 | 323.7428 | -20.2715 | -20.3 | 1057 | 44.0417
| 1058 | -20.2715 | 323.3304 | -20.2967 | -20.3 | 1058 | 44.0833
| 1059 | -20.2967 | 322.9185 | -20.3218 | -20.3 | 1059 | 44.125
| 1060 | -20.3218 | 322.5071 | -20.3469 | -20.3 | 1060 | 44.1667
| 1061 | -20.3469 | 322.0963 | -20.3719 | -20.4 | 1061 | 44.2083
| 1062 | -20.3719 | 321.6859 | -20.3969 | -20.4 | 1062 | 44.25
| 1063 | -20.3969 | 321.2761 | -20.4219 | -20.4 | 1063 | 44.2917
| 1064 | -20.4219 | 320.8669 | -20.4468 | -20.4 | 1064 | 44.3333
| 1065 | -20.4468 | 320.4581 | -20.4717 | -20.5 | 1065 | 44.375
| 1066 | -20.4717 | 320.0499 | -20.4966 | -20.5 | 1066 | 44.4167
| 1067 | -20.4966 | 319.6421 | -20.5214 | -20.5 | 1067 | 44.4583
| 1068 | -20.5214 | 319.2349 | -20.5463 | -20.5 | 1068 | 44.5
| 1069 | -20.5463 | 318.8283 | -20.571 | -20.6 | 1069 | 44.5417
| 1070 | -20.571 | 318.4221 | -20.5958 | -20.6 | 1070 | 44.5833
| 1071 | -20.5958 | 318.0164 | -20.6205 | -20.6 | 1071 | 44.625
| 1072 | -20.6205 | 317.6113 | -20.6452 | -20.6 | 1072 | 44.6667
| 1073 | -20.6452 | 317.2067 | -20.6699 | -20.7 | 1073 | 44.7083
| 1074 | -20.6699 | 316.8026 | -20.6945 | -20.7 | 1074 | 44.75
| 1075 | -20.6945 | 316.399 | -20.7191 | -20.7 | 1075 | 44.7917
| 1076 | -20.7191 | 315.996 | -20.7436 | -20.7 | 1076 | 44.8333
| 1077 | -20.7436 | 315.5934 | -20.7682 | -20.8 | 1077 | 44.875
| 1078 | -20.7682 | 315.1914 | -20.7927 | -20.8 | 1078 | 44.9167
| 1079 | -20.7927 | 314.7898 | -20.8171 | -20.8 | 1079 | 44.9583
| 1080 | -20.8171 | 314.3888 | -20.8416 | -20.8 | 1080 | 45
| 1081 | -20.8416 | 313.9883 | -20.866 | -20.9 | 1081 | 45.0417
| 1082 | -20.866 | 313.5883 | -20.8904 | -20.9 | 1082 | 45.0833
| 1083 | -20.8904 | 313.1888 | -20.9147 | -20.9 | 1083 | 45.125
| 1084 | -20.9147 | 312.7898 | -20.939 | -20.9 | 1084 | 45.1667
| 1085 | -20.939 | 312.3914 | -20.9633 | -21 | 1085 | 45.2083
| 1086 | -20.9633 | 311.9934 | -20.9875 | -21 | 1086 | 45.25
| 1087 | -20.9875 | 311.5959 | -21.0118 | -21 | 1087 | 45.2917
| 1088 | -21.0118 | 311.199 | -21.036 | -21 | 1088 | 45.3333
| 1089 | -21.036 | 310.8026 | -21.0601 | -21.1 | 1089 | 45.375
| 1090 | -21.0601 | 310.4066 | -21.0842 | -21.1 | 1090 | 45.4167
| 1091 | -21.0842 | 310.0112 | -21.1083 | -21.1 | 1091 | 45.4583
| 1092 | -21.1083 | 309.6163 | -21.1324 | -21.1 | 1092 | 45.5
| 1093 | -21.1324 | 309.2218 | -21.1564 | -21.2 | 1093 | 45.5417
| 1094 | -21.1564 | 308.8279 | -21.1804 | -21.2 | 1094 | 45.5833
| 1095 | -21.1804 | 308.4345 | -21.2044 | -21.2 | 1095 | 45.625
| 1096 | -21.2044 | 308.0416 | -21.2284 | -21.2 | 1096 | 45.6667
| 1097 | -21.2284 | 307.6491 | -21.2523 | -21.3 | 1097 | 45.7083
| 1098 | -21.2523 | 307.2572 | -21.2762 | -21.3 | 1098 | 45.75
| 1099 | -21.2762 | 306.8658 | -21.3 | -21.3 | 1099 | 45.7917
| 1100 | -21.3 | 306.4749 | -21.3238 | -21.3 | 1100 | 45.8333
| 1101 | -21.3238 | 306.0844 | -21.3476 | -21.3 | 1101 | 45.875
| 1102 | -21.3476 | 305.6945 | -21.3714 | -21.4 | 1102 | 45.9167
| 1103 | -21.3714 | 305.3051 | -21.3951 | -21.4 | 1103 | 45.9583
| 1104 | -21.3951 | 304.9161 | -21.4188 | -21.4 | 1104 | 46
| 1105 | -21.4188 | 304.5277 | -21.4425 | -21.4 | 1105 | 46.0417
| 1106 | -21.4425 | 304.1398 | -21.4661 | -21.5 | 1106 | 46.0833
| 1107 | -21.4661 | 303.7523 | -21.4897 | -21.5 | 1107 | 46.125
| 1108 | -21.4897 | 303.3653 | -21.5133 | -21.5 | 1108 | 46.1667
| 1109 | -21.5133 | 302.9789 | -21.5369 | -21.5 | 1109 | 46.2083
| 1110 | -21.5369 | 302.5929 | -21.5604 | -21.6 | 1110 | 46.25
| 1111 | -21.5604 | 302.2074 | -21.5839 | -21.6 | 1111 | 46.2917
| 1112 | -21.5839 | 301.8224 | -21.6073 | -21.6 | 1112 | 46.3333
| 1113 | -21.6073 | 301.4379 | -21.6308 | -21.6 | 1113 | 46.375
| 1114 | -21.6308 | 301.0539 | -21.6542 | -21.7 | 1114 | 46.4167
| 1115 | -21.6542 | 300.6704 | -21.6776 | -21.7 | 1115 | 46.4583
| 1116 | -21.6776 | 300.2874 | -21.7009 | -21.7 | 1116 | 46.5
| 1117 | -21.7009 | 299.9048 | -21.7242 | -21.7 | 1117 | 46.5417
| 1118 | -21.7242 | 299.5228 | -21.7475 | -21.7 | 1118 | 46.5833
| 1119 | -21.7475 | 299.1412 | -21.7707 | -21.8 | 1119 | 46.625
| 1120 | -21.7707 | 298.7601 | -21.794 | -21.8 | 1120 | 46.6667
| 1121 | -21.794 | 298.3795 | -21.8172 | -21.8 | 1121 | 46.7083
| 1122 | -21.8172 | 297.9994 | -21.8403 | -21.8 | 1122 | 46.75
| 1123 | -21.8403 | 297.6198 | -21.8635 | -21.9 | 1123 | 46.7917
| 1124 | -21.8635 | 297.2406 | -21.8866 | -21.9 | 1124 | 46.8333
| 1125 | -21.8866 | 296.862 | -21.9096 | -21.9 | 1125 | 46.875
| 1126 | -21.9096 | 296.4838 | -21.9327 | -21.9 | 1126 | 46.9167
| 1127 | -21.9327 | 296.1061 | -21.9557 | -22 | 1127 | 46.9583
| 1128 | -21.9557 | 295.7289 | -21.9787 | -22 | 1128 | 47
| 1129 | -21.9787 | 295.3521 | -22.0016 | -22 | 1129 | 47.0417
| 1130 | -22.0016 | 294.9759 | -22.0246 | -22 | 1130 | 47.0833
| 1131 | -22.0246 | 294.6001 | -22.0475 | -22 | 1131 | 47.125
| 1132 | -22.0475 | 294.2248 | -22.0703 | -22.1 | 1132 | 47.1667
| 1133 | -22.0703 | 293.85 | -22.0932 | -22.1 | 1133 | 47.2083
| 1134 | -22.0932 | 293.4757 | -22.116 | -22.1 | 1134 | 47.25
| 1135 | -22.116 | 293.1018 | -22.1388 | -22.1 | 1135 | 47.2917
| 1136 | -22.1388 | 292.7284 | -22.1615 | -22.2 | 1136 | 47.3333
| 1137 | -22.1615 | 292.3555 | -22.1843 | -22.2 | 1137 | 47.375
| 1138 | -22.1843 | 291.983 | -22.2069 | -22.2 | 1138 | 47.4167
| 1139 | -22.2069 | 291.6111 | -22.2296 | -22.2 | 1139 | 47.4583
| 1140 | -22.2296 | 291.2396 | -22.2523 | -22.3 | 1140 | 47.5
| 1141 | -22.2523 | 290.8686 | -22.2749 | -22.3 | 1141 | 47.5417
| 1142 | -22.2749 | 290.498 | -22.2974 | -22.3 | 1142 | 47.5833
| 1143 | -22.2974 | 290.128 | -22.32 | -22.3 | 1143 | 47.625
| 1144 | -22.32 | 289.7584 | -22.3425 | -22.3 | 1144 | 47.6667
| 1145 | -22.3425 | 289.3892 | -22.365 | -22.4 | 1145 | 47.7083
| 1146 | -22.365 | 289.0206 | -22.3875 | -22.4 | 1146 | 47.75
| 1147 | -22.3875 | 288.6524 | -22.4099 | -22.4 | 1147 | 47.7917
| 1148 | -22.4099 | 288.2847 | -22.4323 | -22.4 | 1148 | 47.8333
| 1149 | -22.4323 | 287.9174 | -22.4547 | -22.5 | 1149 | 47.875
| 1150 | -22.4547 | 287.5506 | -22.4771 | -22.5 | 1150 | 47.9167
| 1151 | -22.4771 | 287.1843 | -22.4994 | -22.5 | 1151 | 47.9583
| 1152 | -22.4994 | 286.8184 | -22.5217 | -22.5 | 1152 | 48
| 1153 | -22.5217 | 286.4531 | -22.5439 | -22.5 | 1153 | 48.0417
| 1154 | -22.5439 | 286.0881 | -22.5662 | -22.6 | 1154 | 48.0833
| 1155 | -22.5662 | 285.7237 | -22.5884 | -22.6 | 1155 | 48.125
| 1156 | -22.5884 | 285.3597 | -22.6106 | -22.6 | 1156 | 48.1667
| 1157 | -22.6106 | 284.9962 | -22.6327 | -22.6 | 1157 | 48.2083
| 1158 | -22.6327 | 284.6331 | -22.6548 | -22.7 | 1158 | 48.25
| 1159 | -22.6548 | 284.2705 | -22.6769 | -22.7 | 1159 | 48.2917
| 1160 | -22.6769 | 283.9084 | -22.699 | -22.7 | 1160 | 48.3333
| 1161 | -22.699 | 283.5467 | -22.721 | -22.7 | 1161 | 48.375
| 1162 | -22.721 | 283.1855 | -22.7431 | -22.7 | 1162 | 48.4167
| 1163 | -22.7431 | 282.8247 | -22.765 | -22.8 | 1163 | 48.4583
| 1164 | -22.765 | 282.4644 | -22.787 | -22.8 | 1164 | 48.5
| 1165 | -22.787 | 282.1046 | -22.8089 | -22.8 | 1165 | 48.5417
| 1166 | -22.8089 | 281.7452 | -22.8308 | -22.8 | 1166 | 48.5833
| 1167 | -22.8308 | 281.3863 | -22.8527 | -22.9 | 1167 | 48.625
| 1168 | -22.8527 | 281.0278 | -22.8745 | -22.9 | 1168 | 48.6667
| 1169 | -22.8745 | 280.6698 | -22.8964 | -22.9 | 1169 | 48.7083
| 1170 | -22.8964 | 280.3122 | -22.9181 | -22.9 | 1170 | 48.75
| 1171 | -22.9181 | 279.9552 | -22.9399 | -22.9 | 1171 | 48.7917
| 1172 | -22.9399 | 279.5985 | -22.9616 | -23 | 1172 | 48.8333
| 1173 | -22.9616 | 279.2423 | -22.9833 | -23 | 1173 | 48.875
| 1174 | -22.9833 | 278.8866 | -23.005 | -23 | 1174 | 48.9167
| 1175 | -23.005 | 278.5313 | -23.0267 | -23 | 1175 | 48.9583
| 1176 | -23.0267 | 278.1765 | -23.0483 | -23 | 1176 | 49
| 1177 | -23.0483 | 277.8221 | -23.0699 | -23.1 | 1177 | 49.0417
| 1178 | -23.0699 | 277.4682 | -23.0915 | -23.1 | 1178 | 49.0833
| 1179 | -23.0915 | 277.1147 | -23.113 | -23.1 | 1179 | 49.125
| 1180 | -23.113 | 276.7617 | -23.1345 | -23.1 | 1180 | 49.1667
| 1181 | -23.1345 | 276.4091 | -23.156 | -23.2 | 1181 | 49.2083
| 1182 | -23.156 | 276.057 | -23.1775 | -23.2 | 1182 | 49.25
| 1183 | -23.1775 | 275.7053 | -23.1989 | -23.2 | 1183 | 49.2917
| 1184 | -23.1989 | 275.3541 | -23.2203 | -23.2 | 1184 | 49.3333
| 1185 | -23.2203 | 275.0033 | -23.2417 | -23.2 | 1185 | 49.375
| 1186 | -23.2417 | 274.653 | -23.263 | -23.3 | 1186 | 49.4167
| 1187 | -23.263 | 274.3031 | -23.2843 | -23.3 | 1187 | 49.4583
| 1188 | -23.2843 | 273.9536 | -23.3056 | -23.3 | 1188 | 49.5
| 1189 | -23.3056 | 273.6046 | -23.3269 | -23.3 | 1189 | 49.5417
| 1190 | -23.3269 | 273.2561 | -23.3481 | -23.3 | 1190 | 49.5833
| 1191 | -23.3481 | 272.908 | -23.3694 | -23.4 | 1191 | 49.625
| 1192 | -23.3694 | 272.5603 | -23.3905 | -23.4 | 1192 | 49.6667
| 1193 | -23.3905 | 272.2131 | -23.4117 | -23.4 | 1193 | 49.7083
| 1194 | -23.4117 | 271.8663 | -23.4328 | -23.4 | 1194 | 49.75
| 1195 | -23.4328 | 271.52 | -23.4539 | -23.5 | 1195 | 49.7917
| 1196 | -23.4539 | 271.1741 | -23.475 | -23.5 | 1196 | 49.8333
| 1197 | -23.475 | 270.8286 | -23.4961 | -23.5 | 1197 | 49.875
| 1198 | -23.4961 | 270.4836 | -23.5171 | -23.5 | 1198 | 49.9167
| 1199 | -23.5171 | 270.139 | -23.5381 | -23.5 | 1199 | 49.9583
| 1200 | -23.5381 | 269.7949 | -23.5591 | -23.6 | 1200 | 50
| 1201 | -23.5591 | 269.4512 | -23.58 | -23.6 | 1201 | 50.0417
| 1202 | -23.58 | 269.1079 | -23.6009 | -23.6 | 1202 | 50.0833
| 1203 | -23.6009 | 268.7651 | -23.6218 | -23.6 | 1203 | 50.125
| 1204 | -23.6218 | 268.4227 | -23.6427 | -23.6 | 1204 | 50.1667
| 1205 | -23.6427 | 268.0808 | -23.6635 | -23.7 | 1205 | 50.2083
| 1206 | -23.6635 | 267.7393 | -23.6843 | -23.7 | 1206 | 50.25
| 1207 | -23.6843 | 267.3982 | -23.7051 | -23.7 | 1207 | 50.2917
| 1208 | -23.7051 | 267.0575 | -23.7259 | -23.7 | 1208 | 50.3333
| 1209 | -23.7259 | 266.7173 | -23.7466 | -23.7 | 1209 | 50.375
| 1210 | -23.7466 | 266.3776 | -23.7673 | -23.8 | 1210 | 50.4167
| 1211 | -23.7673 | 266.0382 | -23.788 | -23.8 | 1211 | 50.4583
| 1212 | -23.788 | 265.6993 | -23.8086 | -23.8 | 1212 | 50.5
| 1213 | -23.8086 | 265.3608 | -23.8293 | -23.8 | 1213 | 50.5417
| 1214 | -23.8293 | 265.0228 | -23.8499 | -23.8 | 1214 | 50.5833
| 1215 | -23.8499 | 264.6851 | -23.8704 | -23.9 | 1215 | 50.625
| 1216 | -23.8704 | 264.348 | -23.891 | -23.9 | 1216 | 50.6667
| 1217 | -23.891 | 264.0112 | -23.9115 | -23.9 | 1217 | 50.7083
| 1218 | -23.9115 | 263.6749 | -23.932 | -23.9 | 1218 | 50.75
| 1219 | -23.932 | 263.339 | -23.9525 | -24 | 1219 | 50.7917
| 1220 | -23.9525 | 263.0035 | -23.9729 | -24 | 1220 | 50.8333
| 1221 | -23.9729 | 262.6684 | -23.9933 | -24 | 1221 | 50.875
| 1222 | -23.9933 | 262.3338 | -24.0137 | -24 | 1222 | 50.9167
| 1223 | -24.0137 | 261.9996 | -24.0341 | -24 | 1223 | 50.9583
| 1224 | -24.0341 | 261.6659 | -24.0544 | -24.1 | 1224 | 51
| 1225 | -24.0544 | 261.3325 | -24.0747 | -24.1 | 1225 | 51.0417
| 1226 | -24.0747 | 260.9996 | -24.095 | -24.1 | 1226 | 51.0833
| 1227 | -24.095 | 260.6671 | -24.1153 | -24.1 | 1227 | 51.125
| 1228 | -24.1153 | 260.335 | -24.1355 | -24.1 | 1228 | 51.1667
| 1229 | -24.1355 | 260.0034 | -24.1557 | -24.2 | 1229 | 51.2083
| 1230 | -24.1557 | 259.6722 | -24.1759 | -24.2 | 1230 | 51.25
| 1231 | -24.1759 | 259.3414 | -24.1961 | -24.2 | 1231 | 51.2917
| 1232 | -24.1961 | 259.011 | -24.2162 | -24.2 | 1232 | 51.3333
| 1233 | -24.2162 | 258.681 | -24.2363 | -24.2 | 1233 | 51.375
| 1234 | -24.2363 | 258.3515 | -24.2564 | -24.3 | 1234 | 51.4167
| 1235 | -24.2564 | 258.0224 | -24.2765 | -24.3 | 1235 | 51.4583
| 1236 | -24.2765 | 257.6937 | -24.2965 | -24.3 | 1236 | 51.5
| 1237 | -24.2965 | 257.3654 | -24.3165 | -24.3 | 1237 | 51.5417
| 1238 | -24.3165 | 257.0375 | -24.3365 | -24.3 | 1238 | 51.5833
| 1239 | -24.3365 | 256.7101 | -24.3564 | -24.4 | 1239 | 51.625
| 1240 | -24.3564 | 256.383 | -24.3764 | -24.4 | 1240 | 51.6667
| 1241 | -24.3764 | 256.0564 | -24.3963 | -24.4 | 1241 | 51.7083
| 1242 | -24.3963 | 255.7302 | -24.4161 | -24.4 | 1242 | 51.75
| 1243 | -24.4161 | 255.4045 | -24.436 | -24.4 | 1243 | 51.7917
| 1244 | -24.436 | 255.0791 | -24.4558 | -24.5 | 1244 | 51.8333
| 1245 | -24.4558 | 254.7541 | -24.4756 | -24.5 | 1245 | 51.875
| 1246 | -24.4756 | 254.4296 | -24.4954 | -24.5 | 1246 | 51.9167
| 1247 | -24.4954 | 254.1055 | -24.5152 | -24.5 | 1247 | 51.9583
| 1248 | -24.5152 | 253.7818 | -24.5349 | -24.5 | 1248 | 52
| 1249 | -24.5349 | 253.4585 | -24.5546 | -24.6 | 1249 | 52.0417
| 1250 | -24.5546 | 253.1356 | -24.5743 | -24.6 | 1250 | 52.0833
| 1251 | -24.5743 | 252.8131 | -24.5939 | -24.6 | 1251 | 52.125
| 1252 | -24.5939 | 252.491 | -24.6135 | -24.6 | 1252 | 52.1667
| 1253 | -24.6135 | 252.1694 | -24.6331 | -24.6 | 1253 | 52.2083
| 1254 | -24.6331 | 251.8481 | -24.6527 | -24.7 | 1254 | 52.25
| 1255 | -24.6527 | 251.5273 | -24.6723 | -24.7 | 1255 | 52.2917
| 1256 | -24.6723 | 251.2069 | -24.6918 | -24.7 | 1256 | 52.3333
| 1257 | -24.6918 | 250.8869 | -24.7113 | -24.7 | 1257 | 52.375
| 1258 | -24.7113 | 250.5672 | -24.7308 | -24.7 | 1258 | 52.4167
| 1259 | -24.7308 | 250.248 | -24.7502 | -24.8 | 1259 | 52.4583
| 1260 | -24.7502 | 249.9292 | -24.7696 | -24.8 | 1260 | 52.5
| 1261 | -24.7696 | 249.6109 | -24.7891 | -24.8 | 1261 | 52.5417
| 1262 | -24.7891 | 249.2929 | -24.8084 | -24.8 | 1262 | 52.5833
| 1263 | -24.8084 | 248.9753 | -24.8278 | -24.8 | 1263 | 52.625
| 1264 | -24.8278 | 248.6581 | -24.8471 | -24.8 | 1264 | 52.6667
| 1265 | -24.8471 | 248.3413 | -24.8664 | -24.9 | 1265 | 52.7083
| 1266 | -24.8664 | 248.025 | -24.8857 | -24.9 | 1266 | 52.75
| 1267 | -24.8857 | 247.709 | -24.9049 | -24.9 | 1267 | 52.7917
| 1268 | -24.9049 | 247.3934 | -24.9242 | -24.9 | 1268 | 52.8333
| 1269 | -24.9242 | 247.0783 | -24.9434 | -24.9 | 1269 | 52.875
| 1270 | -24.9434 | 246.7635 | -24.9626 | -25 | 1270 | 52.9167
| 1271 | -24.9626 | 246.4492 | -24.9817 | -25 | 1271 | 52.9583
| 1272 | -24.9817 | 246.1352 | -25.0009 | -25 | 1272 | 53
| 1273 | -25.0009 | 245.8216 | -25.02 | -25 | 1273 | 53.0417
| 1274 | -25.02 | 245.5085 | -25.039 | -25 | 1274 | 53.0833
| 1275 | -25.039 | 245.1957 | -25.0581 | -25.1 | 1275 | 53.125
| 1276 | -25.0581 | 244.8834 | -25.0771 | -25.1 | 1276 | 53.1667
| 1277 | -25.0771 | 244.5714 | -25.0961 | -25.1 | 1277 | 53.2083
| 1278 | -25.0961 | 244.2598 | -25.1151 | -25.1 | 1278 | 53.25
| 1279 | -25.1151 | 243.9487 | -25.1341 | -25.1 | 1279 | 53.2917
| 1280 | -25.1341 | 243.6379 | -25.153 | -25.2 | 1280 | 53.3333
| 1281 | -25.153 | 243.3275 | -25.1719 | -25.2 | 1281 | 53.375
| 1282 | -25.1719 | 243.0175 | -25.1908 | -25.2 | 1282 | 53.4167
| 1283 | -25.1908 | 242.708 | -25.2097 | -25.2 | 1283 | 53.4583
| 1284 | -25.2097 | 242.3988 | -25.2285 | -25.2 | 1284 | 53.5
| 1285 | -25.2285 | 242.09 | -25.2474 | -25.2 | 1285 | 53.5417
| 1286 | -25.2474 | 241.7816 | -25.2662 | -25.3 | 1286 | 53.5833
| 1287 | -25.2662 | 241.4736 | -25.2849 | -25.3 | 1287 | 53.625
| 1288 | -25.2849 | 241.1659 | -25.3037 | -25.3 | 1288 | 53.6667
| 1289 | -25.3037 | 240.8587 | -25.3224 | -25.3 | 1289 | 53.7083
| 1290 | -25.3224 | 240.5519 | -25.3411 | -25.3 | 1290 | 53.75
| 1291 | -25.3411 | 240.2454 | -25.3598 | -25.4 | 1291 | 53.7917
| 1292 | -25.3598 | 239.9394 | -25.3784 | -25.4 | 1292 | 53.8333
| 1293 | -25.3784 | 239.6337 | -25.397 | -25.4 | 1293 | 53.875
| 1294 | -25.397 | 239.3284 | -25.4156 | -25.4 | 1294 | 53.9167
| 1295 | -25.4156 | 239.0235 | -25.4342 | -25.4 | 1295 | 53.9583
| 1296 | -25.4342 | 238.719 | -25.4528 | -25.5 | 1296 | 54
| 1297 | -25.4528 | 238.4149 | -25.4713 | -25.5 | 1297 | 54.0417
| 1298 | -25.4713 | 238.1112 | -25.4898 | -25.5 | 1298 | 54.0833
| 1299 | -25.4898 | 237.8079 | -25.5083 | -25.5 | 1299 | 54.125
| 1300 | -25.5083 | 237.5049 | -25.5268 | -25.5 | 1300 | 54.1667
| 1301 | -25.5268 | 237.2024 | -25.5452 | -25.5 | 1301 | 54.2083
| 1302 | -25.5452 | 236.9002 | -25.5636 | -25.6 | 1302 | 54.25
| 1303 | -25.5636 | 236.5984 | -25.582 | -25.6 | 1303 | 54.2917
| 1304 | -25.582 | 236.297 | -25.6004 | -25.6 | 1304 | 54.3333
| 1305 | -25.6004 | 235.996 | -25.6187 | -25.6 | 1305 | 54.375
| 1306 | -25.6187 | 235.6953 | -25.637 | -25.6 | 1306 | 54.4167
| 1307 | -25.637 | 235.3951 | -25.6553 | -25.7 | 1307 | 54.4583
| 1308 | -25.6553 | 235.0952 | -25.6736 | -25.7 | 1308 | 54.5
| 1309 | -25.6736 | 234.7957 | -25.6919 | -25.7 | 1309 | 54.5417
| 1310 | -25.6919 | 234.4966 | -25.7101 | -25.7 | 1310 | 54.5833
| 1311 | -25.7101 | 234.1979 | -25.7283 | -25.7 | 1311 | 54.625
| 1312 | -25.7283 | 233.8995 | -25.7465 | -25.7 | 1312 | 54.6667
| 1313 | -25.7465 | 233.6015 | -25.7646 | -25.8 | 1313 | 54.7083
| 1314 | -25.7646 | 233.3039 | -25.7828 | -25.8 | 1314 | 54.75
| 1315 | -25.7828 | 233.0067 | -25.8009 | -25.8 | 1315 | 54.7917
| 1316 | -25.8009 | 232.7099 | -25.819 | -25.8 | 1316 | 54.8333
| 1317 | -25.819 | 232.4134 | -25.837 | -25.8 | 1317 | 54.875
| 1318 | -25.837 | 232.1174 | -25.8551 | -25.9 | 1318 | 54.9167
| 1319 | -25.8551 | 231.8217 | -25.8731 | -25.9 | 1319 | 54.9583
| 1320 | -25.8731 | 231.5263 | -25.8911 | -25.9 | 1320 | 55
| 1321 | -25.8911 | 231.2314 | -25.9091 | -25.9 | 1321 | 55.0417
| 1322 | -25.9091 | 230.9368 | -25.927 | -25.9 | 1322 | 55.0833
| 1323 | -25.927 | 230.6426 | -25.9449 | -25.9 | 1323 | 55.125
| 1324 | -25.9449 | 230.3488 | -25.9629 | -26 | 1324 | 55.1667
| 1325 | -25.9629 | 230.0554 | -25.9807 | -26 | 1325 | 55.2083
| 1326 | -25.9807 | 229.7623 | -25.9986 | -26 | 1326 | 55.25
| 1327 | -25.9986 | 229.4696 | -26.0164 | -26 | 1327 | 55.2917
| 1328 | -26.0164 | 229.1773 | -26.0342 | -26 | 1328 | 55.3333
| 1329 | -26.0342 | 228.8853 | -26.052 | -26.1 | 1329 | 55.375
| 1330 | -26.052 | 228.5937 | -26.0698 | -26.1 | 1330 | 55.4167
| 1331 | -26.0698 | 228.3025 | -26.0876 | -26.1 | 1331 | 55.4583
| 1332 | -26.0876 | 228.0117 | -26.1053 | -26.1 | 1332 | 55.5
| 1333 | -26.1053 | 227.7212 | -26.123 | -26.1 | 1333 | 55.5417
| 1334 | -26.123 | 227.4311 | -26.1407 | -26.1 | 1334 | 55.5833
| 1335 | -26.1407 | 227.1414 | -26.1583 | -26.2 | 1335 | 55.625
| 1336 | -26.1583 | 226.852 | -26.1759 | -26.2 | 1336 | 55.6667
| 1337 | -26.1759 | 226.563 | -26.1936 | -26.2 | 1337 | 55.7083
| 1338 | -26.1936 | 226.2744 | -26.2111 | -26.2 | 1338 | 55.75
| 1339 | -26.2111 | 225.9861 | -26.2287 | -26.2 | 1339 | 55.7917
| 1340 | -26.2287 | 225.6982 | -26.2463 | -26.2 | 1340 | 55.8333
| 1341 | -26.2463 | 225.4107 | -26.2638 | -26.3 | 1341 | 55.875
| 1342 | -26.2638 | 225.1236 | -26.2813 | -26.3 | 1342 | 55.9167
| 1343 | -26.2813 | 224.8368 | -26.2987 | -26.3 | 1343 | 55.9583
| 1344 | -26.2987 | 224.5503 | -26.3162 | -26.3 | 1344 | 56
| 1345 | -26.3162 | 224.2643 | -26.3336 | -26.3 | 1345 | 56.0417
| 1346 | -26.3336 | 223.9786 | -26.351 | -26.4 | 1346 | 56.0833
| 1347 | -26.351 | 223.6933 | -26.3684 | -26.4 | 1347 | 56.125
| 1348 | -26.3684 | 223.4083 | -26.3858 | -26.4 | 1348 | 56.1667
| 1349 | -26.3858 | 223.1237 | -26.4031 | -26.4 | 1349 | 56.2083
| 1350 | -26.4031 | 222.8394 | -26.4205 | -26.4 | 1350 | 56.25
| 1351 | -26.4205 | 222.5556 | -26.4378 | -26.4 | 1351 | 56.2917
| 1352 | -26.4378 | 222.272 | -26.455 | -26.5 | 1352 | 56.3333
| 1353 | -26.455 | 221.9889 | -26.4723 | -26.5 | 1353 | 56.375
| 1354 | -26.4723 | 221.7061 | -26.4895 | -26.5 | 1354 | 56.4167
| 1355 | -26.4895 | 221.4237 | -26.5067 | -26.5 | 1355 | 56.4583
| 1356 | -26.5067 | 221.1416 | -26.5239 | -26.5 | 1356 | 56.5
| 1357 | -26.5239 | 220.8599 | -26.5411 | -26.5 | 1357 | 56.5417
| 1358 | -26.5411 | 220.5785 | -26.5582 | -26.6 | 1358 | 56.5833
| 1359 | -26.5582 | 220.2975 | -26.5754 | -26.6 | 1359 | 56.625
| 1360 | -26.5754 | 220.0169 | -26.5925 | -26.6 | 1360 | 56.6667
| 1361 | -26.5925 | 219.7366 | -26.6095 | -26.6 | 1361 | 56.7083
| 1362 | -26.6095 | 219.4566 | -26.6266 | -26.6 | 1362 | 56.75
| 1363 | -26.6266 | 219.1771 | -26.6436 | -26.6 | 1363 | 56.7917
| 1364 | -26.6436 | 218.8979 | -26.6607 | -26.7 | 1364 | 56.8333
| 1365 | -26.6607 | 218.619 | -26.6777 | -26.7 | 1365 | 56.875
| 1366 | -26.6777 | 218.3405 | -26.6946 | -26.7 | 1366 | 56.9167
| 1367 | -26.6946 | 218.0623 | -26.7116 | -26.7 | 1367 | 56.9583
| 1368 | -26.7116 | 217.7846 | -26.7285 | -26.7 | 1368 | 57
| 1369 | -26.7285 | 217.5071 | -26.7454 | -26.7 | 1369 | 57.0417
| 1370 | -26.7454 | 217.23 | -26.7623 | -26.8 | 1370 | 57.0833
| 1371 | -26.7623 | 216.9533 | -26.7792 | -26.8 | 1371 | 57.125
| 1372 | -26.7792 | 216.6769 | -26.796 | -26.8 | 1372 | 57.1667
| 1373 | -26.796 | 216.4009 | -26.8128 | -26.8 | 1373 | 57.2083
| 1374 | -26.8128 | 216.1252 | -26.8296 | -26.8 | 1374 | 57.25
| 1375 | -26.8296 | 215.8499 | -26.8464 | -26.8 | 1375 | 57.2917
| 1376 | -26.8464 | 215.5749 | -26.8632 | -26.9 | 1376 | 57.3333
| 1377 | -26.8632 | 215.3003 | -26.8799 | -26.9 | 1377 | 57.375
| 1378 | -26.8799 | 215.026 | -26.8966 | -26.9 | 1378 | 57.4167
| 1379 | -26.8966 | 214.7521 | -26.9133 | -26.9 | 1379 | 57.4583
| 1380 | -26.9133 | 214.4785 | -26.93 | -26.9 | 1380 | 57.5
| 1381 | -26.93 | 214.2053 | -26.9466 | -26.9 | 1381 | 57.5417
| 1382 | -26.9466 | 213.9324 | -26.9632 | -27 | 1382 | 57.5833
| 1383 | -26.9632 | 213.6598 | -26.9799 | -27 | 1383 | 57.625
| 1384 | -26.9799 | 213.3877 | -26.9964 | -27 | 1384 | 57.6667
| 1385 | -26.9964 | 213.1158 | -27.013 | -27 | 1385 | 57.7083
| 1386 | -27.013 | 212.8443 | -27.0296 | -27 | 1386 | 57.75
| 1387 | -27.0296 | 212.5732 | -27.0461 | -27 | 1387 | 57.7917
| 1388 | -27.0461 | 212.3024 | -27.0626 | -27.1 | 1388 | 57.8333
| 1389 | -27.0626 | 212.0319 | -27.0791 | -27.1 | 1389 | 57.875
| 1390 | -27.0791 | 211.7618 | -27.0955 | -27.1 | 1390 | 57.9167
| 1391 | -27.0955 | 211.492 | -27.112 | -27.1 | 1391 | 57.9583
| 1392 | -27.112 | 211.2226 | -27.1284 | -27.1 | 1392 | 58
| 1393 | -27.1284 | 210.9535 | -27.1448 | -27.1 | 1393 | 58.0417
| 1394 | -27.1448 | 210.6848 | -27.1612 | -27.2 | 1394 | 58.0833
| 1395 | -27.1612 | 210.4164 | -27.1775 | -27.2 | 1395 | 58.125
| 1396 | -27.1775 | 210.1483 | -27.1938 | -27.2 | 1396 | 58.1667
| 1397 | -27.1938 | 209.8806 | -27.2102 | -27.2 | 1397 | 58.2083
| 1398 | -27.2102 | 209.6133 | -27.2265 | -27.2 | 1398 | 58.25
| 1399 | -27.2265 | 209.3462 | -27.2427 | -27.2 | 1399 | 58.2917
| 1400 | -27.2427 | 209.0795 | -27.259 | -27.3 | 1400 | 58.3333
| 1401 | -27.259 | 208.8132 | -27.2752 | -27.3 | 1401 | 58.375
| 1402 | -27.2752 | 208.5472 | -27.2914 | -27.3 | 1402 | 58.4167
| 1403 | -27.2914 | 208.2815 | -27.3076 | -27.3 | 1403 | 58.4583
| 1404 | -27.3076 | 208.0162 | -27.3238 | -27.3 | 1404 | 58.5
| 1405 | -27.3238 | 207.7512 | -27.3399 | -27.3 | 1405 | 58.5417
| 1406 | -27.3399 | 207.4865 | -27.3561 | -27.4 | 1406 | 58.5833
| 1407 | -27.3561 | 207.2222 | -27.3722 | -27.4 | 1407 | 58.625
| 1408 | -27.3722 | 206.9582 | -27.3882 | -27.4 | 1408 | 58.6667
| 1409 | -27.3882 | 206.6945 | -27.4043 | -27.4 | 1409 | 58.7083
| 1410 | -27.4043 | 206.4312 | -27.4204 | -27.4 | 1410 | 58.75
| 1411 | -27.4204 | 206.1683 | -27.4364 | -27.4 | 1411 | 58.7917
| 1412 | -27.4364 | 205.9056 | -27.4524 | -27.5 | 1412 | 58.8333
| 1413 | -27.4524 | 205.6433 | -27.4684 | -27.5 | 1413 | 58.875
| 1414 | -27.4684 | 205.3813 | -27.4843 | -27.5 | 1414 | 58.9167
| 1415 | -27.4843 | 205.1197 | -27.5003 | -27.5 | 1415 | 58.9583
| 1416 | -27.5003 | 204.8584 | -27.5162 | -27.5 | 1416 | 59
| 1417 | -27.5162 | 204.5974 | -27.5321 | -27.5 | 1417 | 59.0417
| 1418 | -27.5321 | 204.3368 | -27.548 | -27.5 | 1418 | 59.0833
| 1419 | -27.548 | 204.0765 | -27.5639 | -27.6 | 1419 | 59.125
| 1420 | -27.5639 | 203.8165 | -27.5797 | -27.6 | 1420 | 59.1667
| 1421 | -27.5797 | 203.5568 | -27.5955 | -27.6 | 1421 | 59.2083
| 1422 | -27.5955 | 203.2975 | -27.6113 | -27.6 | 1422 | 59.25
| 1423 | -27.6113 | 203.0385 | -27.6271 | -27.6 | 1423 | 59.2917
| 1424 | -27.6271 | 202.7799 | -27.6429 | -27.6 | 1424 | 59.3333
| 1425 | -27.6429 | 202.5215 | -27.6586 | -27.7 | 1425 | 59.375
| 1426 | -27.6586 | 202.2635 | -27.6743 | -27.7 | 1426 | 59.4167
| 1427 | -27.6743 | 202.0059 | -27.69 | -27.7 | 1427 | 59.4583
| 1428 | -27.69 | 201.7485 | -27.7057 | -27.7 | 1428 | 59.5
| 1429 | -27.7057 | 201.4915 | -27.7214 | -27.7 | 1429 | 59.5417
| 1430 | -27.7214 | 201.2348 | -27.737 | -27.7 | 1430 | 59.5833
| 1431 | -27.737 | 200.9785 | -27.7526 | -27.8 | 1431 | 59.625
| 1432 | -27.7526 | 200.7225 | -27.7682 | -27.8 | 1432 | 59.6667
| 1433 | -27.7682 | 200.4667 | -27.7838 | -27.8 | 1433 | 59.7083
| 1434 | -27.7838 | 200.2114 | -27.7994 | -27.8 | 1434 | 59.75
| 1435 | -27.7994 | 199.9563 | -27.8149 | -27.8 | 1435 | 59.7917
| 1436 | -27.8149 | 199.7016 | -27.8305 | -27.8 | 1436 | 59.8333
| 1437 | -27.8305 | 199.4472 | -27.846 | -27.8 | 1437 | 59.875
| 1438 | -27.846 | 199.1931 | -27.8614 | -27.9 | 1438 | 59.9167
| 1439 | -27.8614 | 198.9393 | -27.8769 | -27.9 | 1439 | 59.9583
| 1440 | -27.8769 | 198.6859 | -27.8923 | -27.9 | 1440 | 60
| 1441 | -27.8923 | 198.4328 | -27.9078 | -27.9 | 1441 | 60.0417
| 1442 | -27.9078 | 198.18 | -27.9232 | -27.9 | 1442 | 60.0833
| 1443 | -27.9232 | 197.9275 | -27.9386 | -27.9 | 1443 | 60.125
| 1444 | -27.9386 | 197.6754 | -27.9539 | -28 | 1444 | 60.1667
| 1445 | -27.9539 | 197.4236 | -27.9693 | -28 | 1445 | 60.2083
| 1446 | -27.9693 | 197.1721 | -27.9846 | -28 | 1446 | 60.25
| 1447 | -27.9846 | 196.9209 | -27.9999 | -28 | 1447 | 60.2917
| 1448 | -27.9999 | 196.67 | -28.0152 | -28 | 1448 | 60.3333
| 1449 | -28.0152 | 196.4195 | -28.0305 | -28 | 1449 | 60.375
| 1450 | -28.0305 | 196.1693 | -28.0457 | -28 | 1450 | 60.4167
| 1451 | -28.0457 | 195.9194 | -28.0609 | -28.1 | 1451 | 60.4583
| 1452 | -28.0609 | 195.6698 | -28.0761 | -28.1 | 1452 | 60.5
| 1453 | -28.0761 | 195.4205 | -28.0913 | -28.1 | 1453 | 60.5417
| 1454 | -28.0913 | 195.1715 | -28.1065 | -28.1 | 1454 | 60.5833
| 1455 | -28.1065 | 194.9229 | -28.1217 | -28.1 | 1455 | 60.625
| 1456 | -28.1217 | 194.6746 | -28.1368 | -28.1 | 1456 | 60.6667
| 1457 | -28.1368 | 194.4266 | -28.1519 | -28.2 | 1457 | 60.7083
| 1458 | -28.1519 | 194.1789 | -28.167 | -28.2 | 1458 | 60.75
| 1459 | -28.167 | 193.9315 | -28.1821 | -28.2 | 1459 | 60.7917
| 1460 | -28.1821 | 193.6845 | -28.1971 | -28.2 | 1460 | 60.8333
| 1461 | -28.1971 | 193.4377 | -28.2122 | -28.2 | 1461 | 60.875
| 1462 | -28.2122 | 193.1913 | -28.2272 | -28.2 | 1462 | 60.9167
| 1463 | -28.2272 | 192.9452 | -28.2422 | -28.2 | 1463 | 60.9583
| 1464 | -28.2422 | 192.6994 | -28.2572 | -28.3 | 1464 | 61
| 1465 | -28.2572 | 192.4539 | -28.2721 | -28.3 | 1465 | 61.0417
| 1466 | -28.2721 | 192.2088 | -28.2871 | -28.3 | 1466 | 61.0833
| 1467 | -28.2871 | 191.9639 | -28.302 | -28.3 | 1467 | 61.125
| 1468 | -28.302 | 191.7194 | -28.3169 | -28.3 | 1468 | 61.1667
| 1469 | -28.3169 | 191.4751 | -28.3318 | -28.3 | 1469 | 61.2083
| 1470 | -28.3318 | 191.2312 | -28.3466 | -28.3 | 1470 | 61.25
| 1471 | -28.3466 | 190.9876 | -28.3615 | -28.4 | 1471 | 61.2917
| 1472 | -28.3615 | 190.7443 | -28.3763 | -28.4 | 1472 | 61.3333
| 1473 | -28.3763 | 190.5013 | -28.3911 | -28.4 | 1473 | 61.375
| 1474 | -28.3911 | 190.2586 | -28.4059 | -28.4 | 1474 | 61.4167
| 1475 | -28.4059 | 190.0162 | -28.4207 | -28.4 | 1475 | 61.4583
| 1476 | -28.4207 | 189.7742 | -28.4354 | -28.4 | 1476 | 61.5
| 1477 | -28.4354 | 189.5324 | -28.4502 | -28.5 | 1477 | 61.5417
| 1478 | -28.4502 | 189.2909 | -28.4649 | -28.5 | 1478 | 61.5833
| 1479 | -28.4649 | 189.0498 | -28.4796 | -28.5 | 1479 | 61.625
| 1480 | -28.4796 | 188.809 | -28.4942 | -28.5 | 1480 | 61.6667
| 1481 | -28.4942 | 188.5684 | -28.5089 | -28.5 | 1481 | 61.7083
| 1482 | -28.5089 | 188.3282 | -28.5235 | -28.5 | 1482 | 61.75
| 1483 | -28.5235 | 188.0883 | -28.5382 | -28.5 | 1483 | 61.7917
| 1484 | -28.5382 | 187.8487 | -28.5528 | -28.6 | 1484 | 61.8333
| 1485 | -28.5528 | 187.6094 | -28.5673 | -28.6 | 1485 | 61.875
| 1486 | -28.5673 | 187.3704 | -28.5819 | -28.6 | 1486 | 61.9167
| 1487 | -28.5819 | 187.1317 | -28.5964 | -28.6 | 1487 | 61.9583
| 1488 | -28.5964 | 186.8933 | -28.611 | -28.6 | 1488 | 62
| 1489 | -28.611 | 186.6552 | -28.6255 | -28.6 | 1489 | 62.0417
| 1490 | -28.6255 | 186.4174 | -28.64 | -28.6 | 1490 | 62.0833
| 1491 | -28.64 | 186.1799 | -28.6544 | -28.7 | 1491 | 62.125
| 1492 | -28.6544 | 185.9428 | -28.6689 | -28.7 | 1492 | 62.1667
| 1493 | -28.6689 | 185.7059 | -28.6833 | -28.7 | 1493 | 62.2083
| 1494 | -28.6833 | 185.4693 | -28.6977 | -28.7 | 1494 | 62.25
| 1495 | -28.6977 | 185.233 | -28.7121 | -28.7 | 1495 | 62.2917
| 1496 | -28.7121 | 184.9971 | -28.7265 | -28.7 | 1496 | 62.3333
| 1497 | -28.7265 | 184.7614 | -28.7409 | -28.7 | 1497 | 62.375
| 1498 | -28.7409 | 184.526 | -28.7552 | -28.8 | 1498 | 62.4167
| 1499 | -28.7552 | 184.2909 | -28.7696 | -28.8 | 1499 | 62.4583
| 1500 | -28.7696 | 184.0562 | -28.7839 | -28.8 | 1500 | 62.5
| 1501 | -28.7839 | 183.8217 | -28.7982 | -28.8 | 1501 | 62.5417
| 1502 | -28.7982 | 183.5875 | -28.8124 | -28.8 | 1502 | 62.5833
| 1503 | -28.8124 | 183.3537 | -28.8267 | -28.8 | 1503 | 62.625
| 1504 | -28.8267 | 183.1201 | -28.8409 | -28.8 | 1504 | 62.6667
| 1505 | -28.8409 | 182.8868 | -28.8551 | -28.9 | 1505 | 62.7083
| 1506 | -28.8551 | 182.6538 | -28.8693 | -28.9 | 1506 | 62.75
| 1507 | -28.8693 | 182.4211 | -28.8835 | -28.9 | 1507 | 62.7917
| 1508 | -28.8835 | 182.1887 | -28.8977 | -28.9 | 1508 | 62.8333
| 1509 | -28.8977 | 181.9566 | -28.9118 | -28.9 | 1509 | 62.875
| 1510 | -28.9118 | 181.7248 | -28.9259 | -28.9 | 1510 | 62.9167
| 1511 | -28.9259 | 181.4933 | -28.94 | -28.9 | 1511 | 62.9583
| 1512 | -28.94 | 181.2621 | -28.9541 | -29 | 1512 | 63
| 1513 | -28.9541 | 181.0312 | -28.9682 | -29 | 1513 | 63.0417
| 1514 | -28.9682 | 180.8006 | -28.9823 | -29 | 1514 | 63.0833
| 1515 | -28.9823 | 180.5703 | -28.9963 | -29 | 1515 | 63.125
| 1516 | -28.9963 | 180.3402 | -29.0103 | -29 | 1516 | 63.1667
| 1517 | -29.0103 | 180.1105 | -29.0243 | -29 | 1517 | 63.2083
| 1518 | -29.0243 | 179.881 | -29.0383 | -29 | 1518 | 63.25
| 1519 | -29.0383 | 179.6519 | -29.0523 | -29.1 | 1519 | 63.2917
| 1520 | -29.0523 | 179.423 | -29.0662 | -29.1 | 1520 | 63.3333
| 1521 | -29.0662 | 179.1945 | -29.0801 | -29.1 | 1521 | 63.375
| 1522 | -29.0801 | 178.9662 | -29.094 | -29.1 | 1522 | 63.4167
| 1523 | -29.094 | 178.7382 | -29.1079 | -29.1 | 1523 | 63.4583
| 1524 | -29.1079 | 178.5105 | -29.1218 | -29.1 | 1524 | 63.5
| 1525 | -29.1218 | 178.2831 | -29.1357 | -29.1 | 1525 | 63.5417
| 1526 | -29.1357 | 178.056 | -29.1495 | -29.1 | 1526 | 63.5833
| 1527 | -29.1495 | 177.8291 | -29.1633 | -29.2 | 1527 | 63.625
| 1528 | -29.1633 | 177.6026 | -29.1771 | -29.2 | 1528 | 63.6667
| 1529 | -29.1771 | 177.3763 | -29.1909 | -29.2 | 1529 | 63.7083
| 1530 | -29.1909 | 177.1504 | -29.2047 | -29.2 | 1530 | 63.75
| 1531 | -29.2047 | 176.9247 | -29.2184 | -29.2 | 1531 | 63.7917
| 1532 | -29.2184 | 176.6993 | -29.2322 | -29.2 | 1532 | 63.8333
| 1533 | -29.2322 | 176.4742 | -29.2459 | -29.2 | 1533 | 63.875
| 1534 | -29.2459 | 176.2494 | -29.2596 | -29.3 | 1534 | 63.9167
| 1535 | -29.2596 | 176.0249 | -29.2733 | -29.3 | 1535 | 63.9583
| 1536 | -29.2733 | 175.8006 | -29.2869 | -29.3 | 1536 | 64
| 1537 | -29.2869 | 175.5767 | -29.3006 | -29.3 | 1537 | 64.0417
| 1538 | -29.3006 | 175.353 | -29.3142 | -29.3 | 1538 | 64.0833
| 1539 | -29.3142 | 175.1296 | -29.3278 | -29.3 | 1539 | 64.125
| 1540 | -29.3278 | 174.9065 | -29.3414 | -29.3 | 1540 | 64.1667
| 1541 | -29.3414 | 174.6837 | -29.355 | -29.4 | 1541 | 64.2083
| 1542 | -29.355 | 174.4611 | -29.3686 | -29.4 | 1542 | 64.25
| 1543 | -29.3686 | 174.2389 | -29.3821 | -29.4 | 1543 | 64.2917
| 1544 | -29.3821 | 174.0169 | -29.3956 | -29.4 | 1544 | 64.3333
| 1545 | -29.3956 | 173.7952 | -29.4092 | -29.4 | 1545 | 64.375
| 1546 | -29.4092 | 173.5738 | -29.4226 | -29.4 | 1546 | 64.4167
| 1547 | -29.4226 | 173.3527 | -29.4361 | -29.4 | 1547 | 64.4583
| 1548 | -29.4361 | 173.1319 | -29.4496 | -29.4 | 1548 | 64.5
| 1549 | -29.4496 | 172.9113 | -29.463 | -29.5 | 1549 | 64.5417
| 1550 | -29.463 | 172.6911 | -29.4764 | -29.5 | 1550 | 64.5833
| 1551 | -29.4764 | 172.4711 | -29.4898 | -29.5 | 1551 | 64.625
| 1552 | -29.4898 | 172.2513 | -29.5032 | -29.5 | 1552 | 64.6667
| 1553 | -29.5032 | 172.0319 | -29.5166 | -29.5 | 1553 | 64.7083
| 1554 | -29.5166 | 171.8128 | -29.53 | -29.5 | 1554 | 64.75
| 1555 | -29.53 | 171.5939 | -29.5433 | -29.5 | 1555 | 64.7917
| 1556 | -29.5433 | 171.3753 | -29.5566 | -29.6 | 1556 | 64.8333
| 1557 | -29.5566 | 171.157 | -29.5699 | -29.6 | 1557 | 64.875
| 1558 | -29.5699 | 170.9389 | -29.5832 | -29.6 | 1558 | 64.9167
| 1559 | -29.5832 | 170.7212 | -29.5965 | -29.6 | 1559 | 64.9583
| 1560 | -29.5965 | 170.5037 | -29.6097 | -29.6 | 1560 | 65
| 1561 | -29.6097 | 170.2865 | -29.623 | -29.6 | 1561 | 65.0417
| 1562 | -29.623 | 170.0695 | -29.6362 | -29.6 | 1562 | 65.0833
| 1563 | -29.6362 | 169.8529 | -29.6494 | -29.6 | 1563 | 65.125
| 1564 | -29.6494 | 169.6365 | -29.6626 | -29.7 | 1564 | 65.1667
| 1565 | -29.6626 | 169.4204 | -29.6757 | -29.7 | 1565 | 65.2083
| 1566 | -29.6757 | 169.2046 | -29.6889 | -29.7 | 1566 | 65.25
| 1567 | -29.6889 | 168.989 | -29.702 | -29.7 | 1567 | 65.2917
| 1568 | -29.702 | 168.7737 | -29.7152 | -29.7 | 1568 | 65.3333
| 1569 | -29.7152 | 168.5587 | -29.7283 | -29.7 | 1569 | 65.375
| 1570 | -29.7283 | 168.344 | -29.7413 | -29.7 | 1570 | 65.4167
| 1571 | -29.7413 | 168.1295 | -29.7544 | -29.8 | 1571 | 65.4583
| 1572 | -29.7544 | 167.9153 | -29.7675 | -29.8 | 1572 | 65.5
| 1573 | -29.7675 | 167.7014 | -29.7805 | -29.8 | 1573 | 65.5417
| 1574 | -29.7805 | 167.4878 | -29.7935 | -29.8 | 1574 | 65.5833
| 1575 | -29.7935 | 167.2744 | -29.8065 | -29.8 | 1575 | 65.625
| 1576 | -29.8065 | 167.0613 | -29.8195 | -29.8 | 1576 | 65.6667
| 1577 | -29.8195 | 166.8485 | -29.8325 | -29.8 | 1577 | 65.7083
| 1578 | -29.8325 | 166.636 | -29.8454 | -29.8 | 1578 | 65.75
| 1579 | -29.8454 | 166.4237 | -29.8584 | -29.9 | 1579 | 65.7917
| 1580 | -29.8584 | 166.2117 | -29.8713 | -29.9 | 1580 | 65.8333
| 1581 | -29.8713 | 165.9999 | -29.8842 | -29.9 | 1581 | 65.875
| 1582 | -29.8842 | 165.7885 | -29.8971 | -29.9 | 1582 | 65.9167
| 1583 | -29.8971 | 165.5773 | -29.9099 | -29.9 | 1583 | 65.9583
| 1584 | -29.9099 | 165.3663 | -29.9228 | -29.9 | 1584 | 66
| 1585 | -29.9228 | 165.1557 | -29.9356 | -29.9 | 1585 | 66.0417
| 1586 | -29.9356 | 164.9453 | -29.9485 | -29.9 | 1586 | 66.0833
| 1587 | -29.9485 | 164.7351 | -29.9613 | -30 | 1587 | 66.125
| 1588 | -29.9613 | 164.5253 | -29.9741 | -30 | 1588 | 66.1667
| 1589 | -29.9741 | 164.3157 | -29.9868 | -30 | 1589 | 66.2083
| 1590 | -29.9868 | 164.1064 | -29.9996 | -30 | 1590 | 66.25
| 1591 | -29.9996 | 163.8973 | -30.0123 | -30 | 1591 | 66.2917
| 1592 | -30.0123 | 163.6885 | -30.025 | -30 | 1592 | 66.3333
| 1593 | -30.025 | 163.48 | -30.0378 | -30 | 1593 | 66.375
| 1594 | -30.0378 | 163.2717 | -30.0504 | -30.1 | 1594 | 66.4167
| 1595 | -30.0504 | 163.0637 | -30.0631 | -30.1 | 1595 | 66.4583
| 1596 | -30.0631 | 162.856 | -30.0758 | -30.1 | 1596 | 66.5
| 1597 | -30.0758 | 162.6485 | -30.0884 | -30.1 | 1597 | 66.5417
| 1598 | -30.0884 | 162.4413 | -30.101 | -30.1 | 1598 | 66.5833
| 1599 | -30.101 | 162.2344 | -30.1137 | -30.1 | 1599 | 66.625
| 1600 | -30.1137 | 162.0277 | -30.1262 | -30.1 | 1600 | 66.6667
| 1601 | -30.1262 | 161.8213 | -30.1388 | -30.1 | 1601 | 66.7083
| 1602 | -30.1388 | 161.6151 | -30.1514 | -30.2 | 1602 | 66.75
| 1603 | -30.1514 | 161.4093 | -30.1639 | -30.2 | 1603 | 66.7917
| 1604 | -30.1639 | 161.2036 | -30.1765 | -30.2 | 1604 | 66.8333
| 1605 | -30.1765 | 160.9983 | -30.189 | -30.2 | 1605 | 66.875
| 1606 | -30.189 | 160.7932 | -30.2015 | -30.2 | 1606 | 66.9167
| 1607 | -30.2015 | 160.5883 | -30.214 | -30.2 | 1607 | 66.9583
| 1608 | -30.214 | 160.3838 | -30.2264 | -30.2 | 1608 | 67
| 1609 | -30.2264 | 160.1794 | -30.2389 | -30.2 | 1609 | 67.0417
| 1610 | -30.2389 | 159.9754 | -30.2513 | -30.3 | 1610 | 67.0833
| 1611 | -30.2513 | 159.7716 | -30.2637 | -30.3 | 1611 | 67.125
| 1612 | -30.2637 | 159.5681 | -30.2761 | -30.3 | 1612 | 67.1667
| 1613 | -30.2761 | 159.3648 | -30.2885 | -30.3 | 1613 | 67.2083
| 1614 | -30.2885 | 159.1618 | -30.3009 | -30.3 | 1614 | 67.25
| 1615 | -30.3009 | 158.959 | -30.3133 | -30.3 | 1615 | 67.2917
| 1616 | -30.3133 | 158.7565 | -30.3256 | -30.3 | 1616 | 67.3333
| 1617 | -30.3256 | 158.5543 | -30.3379 | -30.3 | 1617 | 67.375
| 1618 | -30.3379 | 158.3523 | -30.3502 | -30.4 | 1618 | 67.4167
| 1619 | -30.3502 | 158.1505 | -30.3625 | -30.4 | 1619 | 67.4583
| 1620 | -30.3625 | 157.9491 | -30.3748 | -30.4 | 1620 | 67.5
| 1621 | -30.3748 | 157.7478 | -30.3871 | -30.4 | 1621 | 67.5417
| 1622 | -30.3871 | 157.5469 | -30.3993 | -30.4 | 1622 | 67.5833
| 1623 | -30.3993 | 157.3462 | -30.4115 | -30.4 | 1623 | 67.625
| 1624 | -30.4115 | 157.1457 | -30.4238 | -30.4 | 1624 | 67.6667
| 1625 | -30.4238 | 156.9455 | -30.4359 | -30.4 | 1625 | 67.7083
| 1626 | -30.4359 | 156.7456 | -30.4481 | -30.4 | 1626 | 67.75
| 1627 | -30.4481 | 156.5459 | -30.4603 | -30.5 | 1627 | 67.7917
| 1628 | -30.4603 | 156.3465 | -30.4725 | -30.5 | 1628 | 67.8333
| 1629 | -30.4725 | 156.1473 | -30.4846 | -30.5 | 1629 | 67.875
| 1630 | -30.4846 | 155.9484 | -30.4967 | -30.5 | 1630 | 67.9167
| 1631 | -30.4967 | 155.7497 | -30.5088 | -30.5 | 1631 | 67.9583
| 1632 | -30.5088 | 155.5513 | -30.5209 | -30.5 | 1632 | 68
| 1633 | -30.5209 | 155.3532 | -30.533 | -30.5 | 1633 | 68.0417
| 1634 | -30.533 | 155.1553 | -30.545 | -30.5 | 1634 | 68.0833
| 1635 | -30.545 | 154.9576 | -30.5571 | -30.6 | 1635 | 68.125
| 1636 | -30.5571 | 154.7602 | -30.5691 | -30.6 | 1636 | 68.1667
| 1637 | -30.5691 | 154.563 | -30.5811 | -30.6 | 1637 | 68.2083
| 1638 | -30.5811 | 154.3661 | -30.5931 | -30.6 | 1638 | 68.25
| 1639 | -30.5931 | 154.1695 | -30.6051 | -30.6 | 1639 | 68.2917
| 1640 | -30.6051 | 153.9731 | -30.6171 | -30.6 | 1640 | 68.3333
| 1641 | -30.6171 | 153.7769 | -30.629 | -30.6 | 1641 | 68.375
| 1642 | -30.629 | 153.581 | -30.641 | -30.6 | 1642 | 68.4167
| 1643 | -30.641 | 153.3854 | -30.6529 | -30.7 | 1643 | 68.4583
| 1644 | -30.6529 | 153.19 | -30.6648 | -30.7 | 1644 | 68.5
| 1645 | -30.6648 | 152.9948 | -30.6767 | -30.7 | 1645 | 68.5417
| 1646 | -30.6767 | 152.7999 | -30.6886 | -30.7 | 1646 | 68.5833
| 1647 | -30.6886 | 152.6053 | -30.7004 | -30.7 | 1647 | 68.625
| 1648 | -30.7004 | 152.4109 | -30.7123 | -30.7 | 1648 | 68.6667
| 1649 | -30.7123 | 152.2167 | -30.7241 | -30.7 | 1649 | 68.7083
| 1650 | -30.7241 | 152.0228 | -30.7359 | -30.7 | 1650 | 68.75
| 1651 | -30.7359 | 151.8291 | -30.7477 | -30.7 | 1651 | 68.7917
| 1652 | -30.7477 | 151.6357 | -30.7595 | -30.8 | 1652 | 68.8333
| 1653 | -30.7595 | 151.4425 | -30.7713 | -30.8 | 1653 | 68.875
| 1654 | -30.7713 | 151.2496 | -30.7831 | -30.8 | 1654 | 68.9167
| 1655 | -30.7831 | 151.0569 | -30.7948 | -30.8 | 1655 | 68.9583
| 1656 | -30.7948 | 150.8645 | -30.8065 | -30.8 | 1656 | 69
| 1657 | -30.8065 | 150.6723 | -30.8182 | -30.8 | 1657 | 69.0417
| 1658 | -30.8182 | 150.4804 | -30.8299 | -30.8 | 1658 | 69.0833
| 1659 | -30.8299 | 150.2887 | -30.8416 | -30.8 | 1659 | 69.125
| 1660 | -30.8416 | 150.0972 | -30.8533 | -30.9 | 1660 | 69.1667
| 1661 | -30.8533 | 149.906 | -30.8649 | -30.9 | 1661 | 69.2083
| 1662 | -30.8649 | 149.715 | -30.8766 | -30.9 | 1662 | 69.25
| 1663 | -30.8766 | 149.5243 | -30.8882 | -30.9 | 1663 | 69.2917
| 1664 | -30.8882 | 149.3338 | -30.8998 | -30.9 | 1664 | 69.3333
| 1665 | -30.8998 | 149.1436 | -30.9114 | -30.9 | 1665 | 69.375
| 1666 | -30.9114 | 148.9536 | -30.923 | -30.9 | 1666 | 69.4167
| 1667 | -30.923 | 148.7638 | -30.9345 | -30.9 | 1667 | 69.4583
| 1668 | -30.9345 | 148.5743 | -30.9461 | -30.9 | 1668 | 69.5
| 1669 | -30.9461 | 148.385 | -30.9576 | -31 | 1669 | 69.5417
| 1670 | -30.9576 | 148.196 | -30.9691 | -31 | 1670 | 69.5833
| 1671 | -30.9691 | 148.0072 | -30.9806 | -31 | 1671 | 69.625
| 1672 | -30.9806 | 147.8187 | -30.9921 | -31 | 1672 | 69.6667
| 1673 | -30.9921 | 147.6304 | -31.0036 | -31 | 1673 | 69.7083
| 1674 | -31.0036 | 147.4423 | -31.0151 | -31 | 1674 | 69.75
| 1675 | -31.0151 | 147.2545 | -31.0265 | -31 | 1675 | 69.7917
| 1676 | -31.0265 | 147.0669 | -31.0379 | -31 | 1676 | 69.8333
| 1677 | -31.0379 | 146.8795 | -31.0494 | -31 | 1677 | 69.875
| 1678 | -31.0494 | 146.6924 | -31.0608 | -31.1 | 1678 | 69.9167
| 1679 | -31.0608 | 146.5055 | -31.0722 | -31.1 | 1679 | 69.9583
| 1680 | -31.0722 | 146.3189 | -31.0835 | -31.1 | 1680 | 70
| 1681 | -31.0835 | 146.1325 | -31.0949 | -31.1 | 1681 | 70.0417
| 1682 | -31.0949 | 145.9463 | -31.1062 | -31.1 | 1682 | 70.0833
| 1683 | -31.1062 | 145.7604 | -31.1176 | -31.1 | 1683 | 70.125
| 1684 | -31.1176 | 145.5747 | -31.1289 | -31.1 | 1684 | 70.1667
| 1685 | -31.1289 | 145.3893 | -31.1402 | -31.1 | 1685 | 70.2083
| 1686 | -31.1402 | 145.204 | -31.1515 | -31.2 | 1686 | 70.25
| 1687 | -31.1515 | 145.0191 | -31.1627 | -31.2 | 1687 | 70.2917
| 1688 | -31.1627 | 144.8343 | -31.174 | -31.2 | 1688 | 70.3333
| 1689 | -31.174 | 144.6498 | -31.1852 | -31.2 | 1689 | 70.375
| 1690 | -31.1852 | 144.4655 | -31.1965 | -31.2 | 1690 | 70.4167
| 1691 | -31.1965 | 144.2815 | -31.2077 | -31.2 | 1691 | 70.4583
| 1692 | -31.2077 | 144.0977 | -31.2189 | -31.2 | 1692 | 70.5
| 1693 | -31.2189 | 143.9141 | -31.2301 | -31.2 | 1693 | 70.5417
| 1694 | -31.2301 | 143.7308 | -31.2412 | -31.2 | 1694 | 70.5833
| 1695 | -31.2412 | 143.5477 | -31.2524 | -31.3 | 1695 | 70.625
| 1696 | -31.2524 | 143.3648 | -31.2635 | -31.3 | 1696 | 70.6667
| 1697 | -31.2635 | 143.1822 | -31.2747 | -31.3 | 1697 | 70.7083
| 1698 | -31.2747 | 142.9998 | -31.2858 | -31.3 | 1698 | 70.75
| 1699 | -31.2858 | 142.8176 | -31.2969 | -31.3 | 1699 | 70.7917
| 1700 | -31.2969 | 142.6357 | -31.308 | -31.3 | 1700 | 70.8333
| 1701 | -31.308 | 142.454 | -31.319 | -31.3 | 1701 | 70.875
| 1702 | -31.319 | 142.2725 | -31.3301 | -31.3 | 1702 | 70.9167
| 1703 | -31.3301 | 142.0912 | -31.3412 | -31.3 | 1703 | 70.9583
| 1704 | -31.3412 | 141.9102 | -31.3522 | -31.4 | 1704 | 71
| 1705 | -31.3522 | 141.7295 | -31.3632 | -31.4 | 1705 | 71.0417
| 1706 | -31.3632 | 141.5489 | -31.3742 | -31.4 | 1706 | 71.0833
| 1707 | -31.3742 | 141.3686 | -31.3852 | -31.4 | 1707 | 71.125
| 1708 | -31.3852 | 141.1885 | -31.3962 | -31.4 | 1708 | 71.1667
| 1709 | -31.3962 | 141.0086 | -31.4071 | -31.4 | 1709 | 71.2083
| 1710 | -31.4071 | 140.829 | -31.4181 | -31.4 | 1710 | 71.25
| 1711 | -31.4181 | 140.6496 | -31.429 | -31.4 | 1711 | 71.2917
| 1712 | -31.429 | 140.4704 | -31.4399 | -31.4 | 1712 | 71.3333
| 1713 | -31.4399 | 140.2915 | -31.4508 | -31.5 | 1713 | 71.375
| 1714 | -31.4508 | 140.1127 | -31.4617 | -31.5 | 1714 | 71.4167
| 1715 | -31.4617 | 139.9342 | -31.4726 | -31.5 | 1715 | 71.4583
| 1716 | -31.4726 | 139.756 | -31.4835 | -31.5 | 1716 | 71.5
| 1717 | -31.4835 | 139.5779 | -31.4943 | -31.5 | 1717 | 71.5417
| 1718 | -31.4943 | 139.4001 | -31.5051 | -31.5 | 1718 | 71.5833
| 1719 | -31.5051 | 139.2225 | -31.516 | -31.5 | 1719 | 71.625
| 1720 | -31.516 | 139.0452 | -31.5268 | -31.5 | 1720 | 71.6667
| 1721 | -31.5268 | 138.868 | -31.5376 | -31.5 | 1721 | 71.7083
| 1722 | -31.5376 | 138.6911 | -31.5483 | -31.5 | 1722 | 71.75
| 1723 | -31.5483 | 138.5145 | -31.5591 | -31.6 | 1723 | 71.7917
| 1724 | -31.5591 | 138.338 | -31.5699 | -31.6 | 1724 | 71.8333
| 1725 | -31.5699 | 138.1618 | -31.5806 | -31.6 | 1725 | 71.875
| 1726 | -31.5806 | 137.9858 | -31.5913 | -31.6 | 1726 | 71.9167
| 1727 | -31.5913 | 137.81 | -31.602 | -31.6 | 1727 | 71.9583
| 1728 | -31.602 | 137.6344 | -31.6127 | -31.6 | 1728 | 72
| 1729 | -31.6127 | 137.4591 | -31.6234 | -31.6 | 1729 | 72.0417
| 1730 | -31.6234 | 137.284 | -31.6341 | -31.6 | 1730 | 72.0833
| 1731 | -31.6341 | 137.1091 | -31.6448 | -31.6 | 1731 | 72.125
| 1732 | -31.6448 | 136.9344 | -31.6554 | -31.7 | 1732 | 72.1667
| 1733 | -31.6554 | 136.76 | -31.666 | -31.7 | 1733 | 72.2083
| 1734 | -31.666 | 136.5857 | -31.6766 | -31.7 | 1734 | 72.25
| 1735 | -31.6766 | 136.4117 | -31.6873 | -31.7 | 1735 | 72.2917
| 1736 | -31.6873 | 136.238 | -31.6978 | -31.7 | 1736 | 72.3333
| 1737 | -31.6978 | 136.0644 | -31.7084 | -31.7 | 1737 | 72.375
| 1738 | -31.7084 | 135.8911 | -31.719 | -31.7 | 1738 | 72.4167
| 1739 | -31.719 | 135.718 | -31.7295 | -31.7 | 1739 | 72.4583
| 1740 | -31.7295 | 135.5451 | -31.7401 | -31.7 | 1740 | 72.5
| 1741 | -31.7401 | 135.3724 | -31.7506 | -31.8 | 1741 | 72.5417
| 1742 | -31.7506 | 135.1999 | -31.7611 | -31.8 | 1742 | 72.5833
| 1743 | -31.7611 | 135.0277 | -31.7716 | -31.8 | 1743 | 72.625
| 1744 | -31.7716 | 134.8557 | -31.7821 | -31.8 | 1744 | 72.6667
| 1745 | -31.7821 | 134.6839 | -31.7925 | -31.8 | 1745 | 72.7083
| 1746 | -31.7925 | 134.5123 | -31.803 | -31.8 | 1746 | 72.75
| 1747 | -31.803 | 134.341 | -31.8134 | -31.8 | 1747 | 72.7917
| 1748 | -31.8134 | 134.1698 | -31.8239 | -31.8 | 1748 | 72.8333
| 1749 | -31.8239 | 133.9989 | -31.8343 | -31.8 | 1749 | 72.875
| 1750 | -31.8343 | 133.8282 | -31.8447 | -31.8 | 1750 | 72.9167
| 1751 | -31.8447 | 133.6577 | -31.8551 | -31.9 | 1751 | 72.9583
| 1752 | -31.8551 | 133.4874 | -31.8655 | -31.9 | 1752 | 73
| 1753 | -31.8655 | 133.3174 | -31.8758 | -31.9 | 1753 | 73.0417
| 1754 | -31.8758 | 133.1475 | -31.8862 | -31.9 | 1754 | 73.0833
| 1755 | -31.8862 | 132.9779 | -31.8965 | -31.9 | 1755 | 73.125
| 1756 | -31.8965 | 132.8085 | -31.9068 | -31.9 | 1756 | 73.1667
| 1757 | -31.9068 | 132.6393 | -31.9171 | -31.9 | 1757 | 73.2083
| 1758 | -31.9171 | 132.4704 | -31.9274 | -31.9 | 1758 | 73.25
| 1759 | -31.9274 | 132.3016 | -31.9377 | -31.9 | 1759 | 73.2917
| 1760 | -31.9377 | 132.1331 | -31.948 | -31.9 | 1760 | 73.3333
| 1761 | -31.948 | 131.9647 | -31.9582 | -32 | 1761 | 73.375
| 1762 | -31.9582 | 131.7966 | -31.9685 | -32 | 1762 | 73.4167
| 1763 | -31.9685 | 131.6287 | -31.9787 | -32 | 1763 | 73.4583
| 1764 | -31.9787 | 131.461 | -31.9889 | -32 | 1764 | 73.5
| 1765 | -31.9889 | 131.2936 | -31.9991 | -32 | 1765 | 73.5417
| 1766 | -31.9991 | 131.1263 | -32.0093 | -32 | 1766 | 73.5833
| 1767 | -32.0093 | 130.9593 | -32.0195 | -32 | 1767 | 73.625
| 1768 | -32.0195 | 130.7924 | -32.0297 | -32 | 1768 | 73.6667
| 1769 | -32.0297 | 130.6258 | -32.0398 | -32 | 1769 | 73.7083
| 1770 | -32.0398 | 130.4594 | -32.05 | -32 | 1770 | 73.75
| 1771 | -32.05 | 130.2932 | -32.0601 | -32.1 | 1771 | 73.7917
| 1772 | -32.0601 | 130.1272 | -32.0702 | -32.1 | 1772 | 73.8333
| 1773 | -32.0702 | 129.9615 | -32.0803 | -32.1 | 1773 | 73.875
| 1774 | -32.0803 | 129.7959 | -32.0904 | -32.1 | 1774 | 73.9167
| 1775 | -32.0904 | 129.6305 | -32.1005 | -32.1 | 1775 | 73.9583
| 1776 | -32.1005 | 129.4654 | -32.1106 | -32.1 | 1776 | 74
| 1777 | -32.1106 | 129.3005 | -32.1206 | -32.1 | 1777 | 74.0417
| 1778 | -32.1206 | 129.1358 | -32.1306 | -32.1 | 1778 | 74.0833
| 1779 | -32.1306 | 128.9712 | -32.1407 | -32.1 | 1779 | 74.125
| 1780 | -32.1407 | 128.8069 | -32.1507 | -32.2 | 1780 | 74.1667
| 1781 | -32.1507 | 128.6429 | -32.1607 | -32.2 | 1781 | 74.2083
| 1782 | -32.1607 | 128.479 | -32.1707 | -32.2 | 1782 | 74.25
| 1783 | -32.1707 | 128.3153 | -32.1806 | -32.2 | 1783 | 74.2917
| 1784 | -32.1806 | 128.1518 | -32.1906 | -32.2 | 1784 | 74.3333
| 1785 | -32.1906 | 127.9886 | -32.2005 | -32.2 | 1785 | 74.375
| 1786 | -32.2005 | 127.8255 | -32.2105 | -32.2 | 1786 | 74.4167
| 1787 | -32.2105 | 127.6627 | -32.2204 | -32.2 | 1787 | 74.4583
| 1788 | -32.2204 | 127.5001 | -32.2303 | -32.2 | 1788 | 74.5
| 1789 | -32.2303 | 127.3376 | -32.2402 | -32.2 | 1789 | 74.5417
| 1790 | -32.2402 | 127.1754 | -32.2501 | -32.3 | 1790 | 74.5833
| 1791 | -32.2501 | 127.0134 | -32.26 | -32.3 | 1791 | 74.625
| 1792 | -32.26 | 126.8516 | -32.2698 | -32.3 | 1792 | 74.6667
| 1793 | -32.2698 | 126.69 | -32.2797 | -32.3 | 1793 | 74.7083
| 1794 | -32.2797 | 126.5286 | -32.2895 | -32.3 | 1794 | 74.75
| 1795 | -32.2895 | 126.3674 | -32.2993 | -32.3 | 1795 | 74.7917
| 1796 | -32.2993 | 126.2064 | -32.3091 | -32.3 | 1796 | 74.8333
| 1797 | -32.3091 | 126.0457 | -32.3189 | -32.3 | 1797 | 74.875
| 1798 | -32.3189 | 125.8851 | -32.3287 | -32.3 | 1798 | 74.9167
| 1799 | -32.3287 | 125.7247 | -32.3385 | -32.3 | 1799 | 74.9583
| 1800 | -32.3385 | 125.5646 | -32.3483 | -32.3 | 1800 | 75
| 1801 | -32.3483 | 125.4046 | -32.358 | -32.4 | 1801 | 75.0417
| 1802 | -32.358 | 125.2448 | -32.3677 | -32.4 | 1802 | 75.0833
| 1803 | -32.3677 | 125.0853 | -32.3775 | -32.4 | 1803 | 75.125
| 1804 | -32.3775 | 124.9259 | -32.3872 | -32.4 | 1804 | 75.1667
| 1805 | -32.3872 | 124.7668 | -32.3969 | -32.4 | 1805 | 75.2083
| 1806 | -32.3969 | 124.6078 | -32.4066 | -32.4 | 1806 | 75.25
| 1807 | -32.4066 | 124.4491 | -32.4162 | -32.4 | 1807 | 75.2917
| 1808 | -32.4162 | 124.2906 | -32.4259 | -32.4 | 1808 | 75.3333
| 1809 | -32.4259 | 124.1322 | -32.4355 | -32.4 | 1809 | 75.375
| 1810 | -32.4355 | 123.9741 | -32.4452 | -32.4 | 1810 | 75.4167
| 1811 | -32.4452 | 123.8162 | -32.4548 | -32.5 | 1811 | 75.4583
| 1812 | -32.4548 | 123.6584 | -32.4644 | -32.5 | 1812 | 75.5
| 1813 | -32.4644 | 123.5009 | -32.474 | -32.5 | 1813 | 75.5417
| 1814 | -32.474 | 123.3436 | -32.4836 | -32.5 | 1814 | 75.5833
| 1815 | -32.4836 | 123.1864 | -32.4932 | -32.5 | 1815 | 75.625
| 1816 | -32.4932 | 123.0295 | -32.5027 | -32.5 | 1816 | 75.6667
| 1817 | -32.5027 | 122.8728 | -32.5123 | -32.5 | 1817 | 75.7083
| 1818 | -32.5123 | 122.7162 | -32.5218 | -32.5 | 1818 | 75.75
| 1819 | -32.5218 | 122.5599 | -32.5314 | -32.5 | 1819 | 75.7917
| 1820 | -32.5314 | 122.4038 | -32.5409 | -32.5 | 1820 | 75.8333
| 1821 | -32.5409 | 122.2478 | -32.5504 | -32.6 | 1821 | 75.875
| 1822 | -32.5504 | 122.0921 | -32.5599 | -32.6 | 1822 | 75.9167
| 1823 | -32.5599 | 121.9366 | -32.5693 | -32.6 | 1823 | 75.9583
| 1824 | -32.5693 | 121.7812 | -32.5788 | -32.6 | 1824 | 76
| 1825 | -32.5788 | 121.6261 | -32.5883 | -32.6 | 1825 | 76.0417
| 1826 | -32.5883 | 121.4712 | -32.5977 | -32.6 | 1826 | 76.0833
| 1827 | -32.5977 | 121.3164 | -32.6071 | -32.6 | 1827 | 76.125
| 1828 | -32.6071 | 121.1619 | -32.6166 | -32.6 | 1828 | 76.1667
| 1829 | -32.6166 | 121.0075 | -32.626 | -32.6 | 1829 | 76.2083
| 1830 | -32.626 | 120.8534 | -32.6354 | -32.6 | 1830 | 76.25
| 1831 | -32.6354 | 120.6994 | -32.6447 | -32.6 | 1831 | 76.2917
| 1832 | -32.6447 | 120.5456 | -32.6541 | -32.7 | 1832 | 76.3333
| 1833 | -32.6541 | 120.3921 | -32.6635 | -32.7 | 1833 | 76.375
| 1834 | -32.6635 | 120.2387 | -32.6728 | -32.7 | 1834 | 76.4167
| 1835 | -32.6728 | 120.0855 | -32.6821 | -32.7 | 1835 | 76.4583
| 1836 | -32.6821 | 119.9325 | -32.6915 | -32.7 | 1836 | 76.5
| 1837 | -32.6915 | 119.7798 | -32.7008 | -32.7 | 1837 | 76.5417
| 1838 | -32.7008 | 119.6272 | -32.7101 | -32.7 | 1838 | 76.5833
| 1839 | -32.7101 | 119.4748 | -32.7194 | -32.7 | 1839 | 76.625
| 1840 | -32.7194 | 119.3226 | -32.7286 | -32.7 | 1840 | 76.6667
| 1841 | -32.7286 | 119.1706 | -32.7379 | -32.7 | 1841 | 76.7083
| 1842 | -32.7379 | 119.0187 | -32.7472 | -32.7 | 1842 | 76.75
| 1843 | -32.7472 | 118.8671 | -32.7564 | -32.8 | 1843 | 76.7917
| 1844 | -32.7564 | 118.7157 | -32.7656 | -32.8 | 1844 | 76.8333
| 1845 | -32.7656 | 118.5645 | -32.7748 | -32.8 | 1845 | 76.875
| 1846 | -32.7748 | 118.4134 | -32.784 | -32.8 | 1846 | 76.9167
| 1847 | -32.784 | 118.2626 | -32.7932 | -32.8 | 1847 | 76.9583
| 1848 | -32.7932 | 118.1119 | -32.8024 | -32.8 | 1848 | 77
| 1849 | -32.8024 | 117.9615 | -32.8116 | -32.8 | 1849 | 77.0417
| 1850 | -32.8116 | 117.8112 | -32.8207 | -32.8 | 1850 | 77.0833
| 1851 | -32.8207 | 117.6611 | -32.8299 | -32.8 | 1851 | 77.125
| 1852 | -32.8299 | 117.5112 | -32.839 | -32.8 | 1852 | 77.1667
| 1853 | -32.839 | 117.3615 | -32.8481 | -32.8 | 1853 | 77.2083
| 1854 | -32.8481 | 117.212 | -32.8573 | -32.9 | 1854 | 77.25
| 1855 | -32.8573 | 117.0627 | -32.8664 | -32.9 | 1855 | 77.2917
| 1856 | -32.8664 | 116.9135 | -32.8754 | -32.9 | 1856 | 77.3333
| 1857 | -32.8754 | 116.7646 | -32.8845 | -32.9 | 1857 | 77.375
| 1858 | -32.8845 | 116.6159 | -32.8936 | -32.9 | 1858 | 77.4167
| 1859 | -32.8936 | 116.4673 | -32.9026 | -32.9 | 1859 | 77.4583
| 1860 | -32.9026 | 116.3189 | -32.9117 | -32.9 | 1860 | 77.5
| 1861 | -32.9117 | 116.1707 | -32.9207 | -32.9 | 1861 | 77.5417
| 1862 | -32.9207 | 116.0228 | -32.9297 | -32.9 | 1862 | 77.5833
| 1863 | -32.9297 | 115.8749 | -32.9387 | -32.9 | 1863 | 77.625
| 1864 | -32.9387 | 115.7273 | -32.9477 | -32.9 | 1864 | 77.6667
| 1865 | -32.9477 | 115.5799 | -32.9567 | -33 | 1865 | 77.7083
| 1866 | -32.9567 | 115.4327 | -32.9657 | -33 | 1866 | 77.75
| 1867 | -32.9657 | 115.2856 | -32.9747 | -33 | 1867 | 77.7917
| 1868 | -32.9747 | 115.1387 | -32.9836 | -33 | 1868 | 77.8333
| 1869 | -32.9836 | 114.9921 | -32.9925 | -33 | 1869 | 77.875
| 1870 | -32.9925 | 114.8456 | -33.0015 | -33 | 1870 | 77.9167
| 1871 | -33.0015 | 114.6993 | -33.0104 | -33 | 1871 | 77.9583
| 1872 | -33.0104 | 114.5532 | -33.0193 | -33 | 1872 | 78
| 1873 | -33.0193 | 114.4072 | -33.0282 | -33 | 1873 | 78.0417
| 1874 | -33.0282 | 114.2615 | -33.0371 | -33 | 1874 | 78.0833
| 1875 | -33.0371 | 114.1159 | -33.0459 | -33 | 1875 | 78.125
| 1876 | -33.0459 | 113.9705 | -33.0548 | -33.1 | 1876 | 78.1667
| 1877 | -33.0548 | 113.8253 | -33.0636 | -33.1 | 1877 | 78.2083
| 1878 | -33.0636 | 113.6803 | -33.0725 | -33.1 | 1878 | 78.25
| 1879 | -33.0725 | 113.5355 | -33.0813 | -33.1 | 1879 | 78.2917
| 1880 | -33.0813 | 113.3909 | -33.0901 | -33.1 | 1880 | 78.3333
| 1881 | -33.0901 | 113.2464 | -33.0989 | -33.1 | 1881 | 78.375
| 1882 | -33.0989 | 113.1022 | -33.1077 | -33.1 | 1882 | 78.4167
| 1883 | -33.1077 | 112.9581 | -33.1165 | -33.1 | 1883 | 78.4583
| 1884 | -33.1165 | 112.8142 | -33.1253 | -33.1 | 1884 | 78.5
| 1885 | -33.1253 | 112.6705 | -33.134 | -33.1 | 1885 | 78.5417
| 1886 | -33.134 | 112.5269 | -33.1428 | -33.1 | 1886 | 78.5833
| 1887 | -33.1428 | 112.3836 | -33.1515 | -33.2 | 1887 | 78.625
| 1888 | -33.1515 | 112.2404 | -33.1602 | -33.2 | 1888 | 78.6667
| 1889 | -33.1602 | 112.0974 | -33.1689 | -33.2 | 1889 | 78.7083
| 1890 | -33.1689 | 111.9546 | -33.1776 | -33.2 | 1890 | 78.75
| 1891 | -33.1776 | 111.812 | -33.1863 | -33.2 | 1891 | 78.7917
| 1892 | -33.1863 | 111.6696 | -33.195 | -33.2 | 1892 | 78.8333
| 1893 | -33.195 | 111.5273 | -33.2037 | -33.2 | 1893 | 78.875
| 1894 | -33.2037 | 111.3852 | -33.2123 | -33.2 | 1894 | 78.9167
| 1895 | -33.2123 | 111.2433 | -33.221 | -33.2 | 1895 | 78.9583
| 1896 | -33.221 | 111.1016 | -33.2296 | -33.2 | 1896 | 79
| 1897 | -33.2296 | 110.9601 | -33.2382 | -33.2 | 1897 | 79.0417
| 1898 | -33.2382 | 110.8187 | -33.2469 | -33.2 | 1898 | 79.0833
| 1899 | -33.2469 | 110.6776 | -33.2555 | -33.3 | 1899 | 79.125
| 1900 | -33.2555 | 110.5366 | -33.2641 | -33.3 | 1900 | 79.1667
| 1901 | -33.2641 | 110.3957 | -33.2726 | -33.3 | 1901 | 79.2083
| 1902 | -33.2726 | 110.2551 | -33.2812 | -33.3 | 1902 | 79.25
| 1903 | -33.2812 | 110.1146 | -33.2898 | -33.3 | 1903 | 79.2917
| 1904 | -33.2898 | 109.9744 | -33.2983 | -33.3 | 1904 | 79.3333
| 1905 | -33.2983 | 109.8343 | -33.3068 | -33.3 | 1905 | 79.375
| 1906 | -33.3068 | 109.6944 | -33.3154 | -33.3 | 1906 | 79.4167
| 1907 | -33.3154 | 109.5546 | -33.3239 | -33.3 | 1907 | 79.4583
| 1908 | -33.3239 | 109.415 | -33.3324 | -33.3 | 1908 | 79.5
| 1909 | -33.3324 | 109.2757 | -33.3409 | -33.3 | 1909 | 79.5417
| 1910 | -33.3409 | 109.1365 | -33.3494 | -33.3 | 1910 | 79.5833
| 1911 | -33.3494 | 108.9974 | -33.3578 | -33.4 | 1911 | 79.625
| 1912 | -33.3578 | 108.8586 | -33.3663 | -33.4 | 1912 | 79.6667
| 1913 | -33.3663 | 108.7199 | -33.3748 | -33.4 | 1913 | 79.7083
| 1914 | -33.3748 | 108.5814 | -33.3832 | -33.4 | 1914 | 79.75
| 1915 | -33.3832 | 108.4431 | -33.3916 | -33.4 | 1915 | 79.7917
| 1916 | -33.3916 | 108.3049 | -33.4 | -33.4 | 1916 | 79.8333
| 1917 | -33.4 | 108.1669 | -33.4085 | -33.4 | 1917 | 79.875
| 1918 | -33.4085 | 108.0291 | -33.4168 | -33.4 | 1918 | 79.9167
| 1919 | -33.4168 | 107.8915 | -33.4252 | -33.4 | 1919 | 79.9583
| 1920 | -33.4252 | 107.7541 | -33.4336 | -33.4 | 1920 | 80
| 1921 | -33.4336 | 107.6168 | -33.442 | -33.4 | 1921 | 80.0417
| 1922 | -33.442 | 107.4797 | -33.4503 | -33.5 | 1922 | 80.0833
| 1923 | -33.4503 | 107.3428 | -33.4587 | -33.5 | 1923 | 80.125
| 1924 | -33.4587 | 107.206 | -33.467 | -33.5 | 1924 | 80.1667
| 1925 | -33.467 | 107.0695 | -33.4753 | -33.5 | 1925 | 80.2083
| 1926 | -33.4753 | 106.9331 | -33.4836 | -33.5 | 1926 | 80.25
| 1927 | -33.4836 | 106.7968 | -33.4919 | -33.5 | 1927 | 80.2917
| 1928 | -33.4919 | 106.6608 | -33.5002 | -33.5 | 1928 | 80.3333
| 1929 | -33.5002 | 106.5249 | -33.5085 | -33.5 | 1929 | 80.375
| 1930 | -33.5085 | 106.3892 | -33.5168 | -33.5 | 1930 | 80.4167
| 1931 | -33.5168 | 106.2537 | -33.525 | -33.5 | 1931 | 80.4583
| 1932 | -33.525 | 106.1183 | -33.5333 | -33.5 | 1932 | 80.5
| 1933 | -33.5333 | 105.9831 | -33.5415 | -33.5 | 1933 | 80.5417
| 1934 | -33.5415 | 105.8481 | -33.5498 | -33.5 | 1934 | 80.5833
| 1935 | -33.5498 | 105.7133 | -33.558 | -33.6 | 1935 | 80.625
| 1936 | -33.558 | 105.5786 | -33.5662 | -33.6 | 1936 | 80.6667
| 1937 | -33.5662 | 105.4441 | -33.5744 | -33.6 | 1937 | 80.7083
| 1938 | -33.5744 | 105.3098 | -33.5826 | -33.6 | 1938 | 80.75
| 1939 | -33.5826 | 105.1756 | -33.5907 | -33.6 | 1939 | 80.7917
| 1940 | -33.5907 | 105.0416 | -33.5989 | -33.6 | 1940 | 80.8333
| 1941 | -33.5989 | 104.9078 | -33.6071 | -33.6 | 1941 | 80.875
| 1942 | -33.6071 | 104.7742 | -33.6152 | -33.6 | 1942 | 80.9167
| 1943 | -33.6152 | 104.6407 | -33.6233 | -33.6 | 1943 | 80.9583
| 1944 | -33.6233 | 104.5074 | -33.6315 | -33.6 | 1944 | 81
| 1945 | -33.6315 | 104.3743 | -33.6396 | -33.6 | 1945 | 81.0417
| 1946 | -33.6396 | 104.2413 | -33.6477 | -33.6 | 1946 | 81.0833
| 1947 | -33.6477 | 104.1085 | -33.6558 | -33.7 | 1947 | 81.125
| 1948 | -33.6558 | 103.9759 | -33.6638 | -33.7 | 1948 | 81.1667
| 1949 | -33.6638 | 103.8434 | -33.6719 | -33.7 | 1949 | 81.2083
| 1950 | -33.6719 | 103.7111 | -33.68 | -33.7 | 1950 | 81.25
| 1951 | -33.68 | 103.579 | -33.688 | -33.7 | 1951 | 81.2917
| 1952 | -33.688 | 103.4471 | -33.6961 | -33.7 | 1952 | 81.3333
| 1953 | -33.6961 | 103.3153 | -33.7041 | -33.7 | 1953 | 81.375
| 1954 | -33.7041 | 103.1837 | -33.7121 | -33.7 | 1954 | 81.4167
| 1955 | -33.7121 | 103.0522 | -33.7201 | -33.7 | 1955 | 81.4583
| 1956 | -33.7201 | 102.9209 | -33.7281 | -33.7 | 1956 | 81.5
| 1957 | -33.7281 | 102.7898 | -33.7361 | -33.7 | 1957 | 81.5417
| 1958 | -33.7361 | 102.6589 | -33.7441 | -33.7 | 1958 | 81.5833
| 1959 | -33.7441 | 102.5281 | -33.7521 | -33.8 | 1959 | 81.625
| 1960 | -33.7521 | 102.3975 | -33.76 | -33.8 | 1960 | 81.6667
| 1961 | -33.76 | 102.267 | -33.768 | -33.8 | 1961 | 81.7083
| 1962 | -33.768 | 102.1368 | -33.7759 | -33.8 | 1962 | 81.75
| 1963 | -33.7759 | 102.0066 | -33.7839 | -33.8 | 1963 | 81.7917
| 1964 | -33.7839 | 101.8767 | -33.7918 | -33.8 | 1964 | 81.8333
| 1965 | -33.7918 | 101.7469 | -33.7997 | -33.8 | 1965 | 81.875
| 1966 | -33.7997 | 101.6173 | -33.8076 | -33.8 | 1966 | 81.9167
| 1967 | -33.8076 | 101.4878 | -33.8155 | -33.8 | 1967 | 81.9583
| 1968 | -33.8155 | 101.3585 | -33.8233 | -33.8 | 1968 | 82
| 1969 | -33.8233 | 101.2294 | -33.8312 | -33.8 | 1969 | 82.0417
| 1970 | -33.8312 | 101.1005 | -33.8391 | -33.8 | 1970 | 82.0833
| 1971 | -33.8391 | 100.9717 | -33.8469 | -33.8 | 1971 | 82.125
| 1972 | -33.8469 | 100.843 | -33.8548 | -33.9 | 1972 | 82.1667
| 1973 | -33.8548 | 100.7146 | -33.8626 | -33.9 | 1973 | 82.2083
| 1974 | -33.8626 | 100.5863 | -33.8704 | -33.9 | 1974 | 82.25
| 1975 | -33.8704 | 100.4581 | -33.8782 | -33.9 | 1975 | 82.2917
| 1976 | -33.8782 | 100.3302 | -33.886 | -33.9 | 1976 | 82.3333
| 1977 | -33.886 | 100.2023 | -33.8938 | -33.9 | 1977 | 82.375
| 1978 | -33.8938 | 100.0747 | -33.9016 | -33.9 | 1978 | 82.4167
| 1979 | -33.9016 | 99.9472 | -33.9094 | -33.9 | 1979 | 82.4583

## How Much Insulation
How long will it take for my water storage to reach freezing temperatures? | [8 empty] | Initial Heat in tank (BTU) | 51460
Note: Cylindrical Tank Calculations; Non-windy conditions only. | [8 empty] | Heat in water = 8.3 BTU/degF-Gal
User Inputs
Tank Size (gal) | 1550 | [7 empty] | rb | 3.625 | ft
Temperature of water at fillup (deg F) | 36 | [7 empty] | rc | 3.7917 | ft
Freezing Temp (deg F) | 32 | [7 empty] | ln(rc/rb) | 0.044951 | unitless
Outside temp (deg F) | -40 | [7 empty] | kinsulation | 0.013889 | (BTU-ft/(hr-ft2-F)
Height of tank (ft) | 5.4167 | [7 empty] | GrPr (air, -40F) | 10^10
Diameter of Tank (ft) | 7.25 | [7 empty] | h (cylinder) | 0.80481
R-value per inch of Insulation | 6 | [7 empty] | Thermal conductivity of insulation (BTU-ft/(hr-ft2-F) | 0.013889
Thickness of insulation (inches) | 2
How much heat was lost during this time? (total BTUs) | 51460
How many hours until danger zone? | 41
How many days? | 1.7083
How many days do want to remain above freezing? | 7
Total BTUS required to achieve this: | 189491.6001
Gallons of sacrificial ice:
How many BTUs must I add to achieve desired storage days? | 138031.6001 |  | 965.2559
How many kWh does this cost me? | 40.4547
If "#N/A" appears, adjust outside temp and or Insulation values.
| Time (hrs) | T1 | Heat lost to environment (BTU/hr) | Temperature of water after 1 hr | Rounded Temp (F) | Time (hrs) | Time (days) | Heat lost to environment (BTU/hr) | Sum of required BTUS
| 0 | 36 | 1245.5671 | 35.9032 | 35.9 | 0 | 0 | 1245.5671 | 1245.5671
| 1 | 35.9032 | 1243.9803 | 35.8065 | 35.8 | 1 | 0.041667 | 1243.9803 | 2489.5474
| 2 | 35.8065 | 1242.3956 | 35.7099 | 35.7 | 2 | 0.083333 | 1242.3956 | 3731.943
| 3 | 35.7099 | 1240.8129 | 35.6135 | 35.6 | 3 | 0.125 | 1240.8129 | 4972.7559
| 4 | 35.6135 | 1239.2322 | 35.5171 | 35.5 | 4 | 0.16667 | 1239.2322 | 6211.9881
| 5 | 35.5171 | 1237.6535 | 35.4209 | 35.4 | 5 | 0.20833 | 1237.6535 | 7449.6416
| 6 | 35.4209 | 1236.0768 | 35.3249 | 35.3 | 6 | 0.25 | 1236.0768 | 8685.7184
| 7 | 35.3249 | 1234.5021 | 35.2289 | 35.2 | 7 | 0.29167 | 1234.5021 | 9920.2205
| 8 | 35.2289 | 1232.9295 | 35.1331 | 35.1 | 8 | 0.33333 | 1232.9295 | 11153.15
| 9 | 35.1331 | 1231.3588 | 35.0373 | 35 | 9 | 0.375 | 1231.3588 | 12384.5088
| 10 | 35.0373 | 1229.7902 | 34.9418 | 34.9 | 10 | 0.41667 | 1229.7902 | 13614.299
| 11 | 34.9418 | 1228.2235 | 34.8463 | 34.8 | 11 | 0.45833 | 1228.2235 | 14842.5225
| 12 | 34.8463 | 1226.6588 | 34.7509 | 34.8 | 12 | 0.5 | 1226.6588 | 16069.1814
| 13 | 34.7509 | 1225.0962 | 34.6557 | 34.7 | 13 | 0.54167 | 1225.0962 | 17294.2775
| 14 | 34.6557 | 1223.5355 | 34.5606 | 34.6 | 14 | 0.58333 | 1223.5355 | 18517.813
| 15 | 34.5606 | 1221.9768 | 34.4656 | 34.5 | 15 | 0.625 | 1221.9768 | 19739.7898
| 16 | 34.4656 | 1220.4201 | 34.3708 | 34.4 | 16 | 0.66667 | 1220.4201 | 20960.2099
| 17 | 34.3708 | 1218.8654 | 34.276 | 34.3 | 17 | 0.70833 | 1218.8654 | 22179.0753
| 18 | 34.276 | 1217.3126 | 34.1814 | 34.2 | 18 | 0.75 | 1217.3126 | 23396.3879
| 19 | 34.1814 | 1215.7619 | 34.0869 | 34.1 | 19 | 0.79167 | 1215.7619 | 24612.1497
| 20 | 34.0869 | 1214.2131 | 33.9925 | 34 | 20 | 0.83333 | 1214.2131 | 25826.3628
| 21 | 33.9925 | 1212.6663 | 33.8982 | 33.9 | 21 | 0.875 | 1212.6663 | 27039.0291
| 22 | 33.8982 | 1211.1214 | 33.8041 | 33.8 | 22 | 0.91667 | 1211.1214 | 28250.1505
| 23 | 33.8041 | 1209.5785 | 33.7101 | 33.7 | 23 | 0.95833 | 1209.5785 | 29459.729
| 24 | 33.7101 | 1208.0376 | 33.6162 | 33.6 | 24 | 1 | 1208.0376 | 30667.7666
| 25 | 33.6162 | 1206.4987 | 33.5224 | 33.5 | 25 | 1.0417 | 1206.4987 | 31874.2653
| 26 | 33.5224 | 1204.9617 | 33.4287 | 33.4 | 26 | 1.0833 | 1204.9617 | 33079.227
| 27 | 33.4287 | 1203.4267 | 33.3352 | 33.3 | 27 | 1.125 | 1203.4267 | 34282.6536
| 28 | 33.3352 | 1201.8936 | 33.2418 | 33.2 | 28 | 1.1667 | 1201.8936 | 35484.5472
| 29 | 33.2418 | 1200.3625 | 33.1485 | 33.1 | 29 | 1.2083 | 1200.3625 | 36684.9097
| 30 | 33.1485 | 1198.8333 | 33.0553 | 33.1 | 30 | 1.25 | 1198.8333 | 37883.743
| 31 | 33.0553 | 1197.3061 | 32.9622 | 33 | 31 | 1.2917 | 1197.3061 | 39081.049
| 32 | 32.9622 | 1195.7808 | 32.8693 | 32.9 | 32 | 1.3333 | 1195.7808 | 40276.8298
| 33 | 32.8693 | 1194.2574 | 32.7764 | 32.8 | 33 | 1.375 | 1194.2574 | 41471.0872
| 34 | 32.7764 | 1192.7361 | 32.6837 | 32.7 | 34 | 1.4167 | 1192.7361 | 42663.8233
| 35 | 32.6837 | 1191.2166 | 32.5911 | 32.6 | 35 | 1.4583 | 1191.2166 | 43855.0399
| 36 | 32.5911 | 1189.6991 | 32.4987 | 32.5 | 36 | 1.5 | 1189.6991 | 45044.739
| 37 | 32.4987 | 1188.1835 | 32.4063 | 32.4 | 37 | 1.5417 | 1188.1835 | 46232.9225
| 38 | 32.4063 | 1186.6698 | 32.3141 | 32.3 | 38 | 1.5833 | 1186.6698 | 47419.5923
| 39 | 32.3141 | 1185.1581 | 32.2219 | 32.2 | 39 | 1.625 | 1185.1581 | 48604.7504
| 40 | 32.2219 | 1183.6483 | 32.1299 | 32.1 | 40 | 1.6667 | 1183.6483 | 49788.3987
| 41 | 32.1299 | 1182.1404 | 32.038 | 32 | 41 | 1.7083 | 1182.1404 | 50970.5391
| 42 | 32.038 | 1180.6345 | 31.9463 | 31.9 | 42 | 1.75 | 1180.6345 | 52151.1736
| 43 | 31.9463 | 1179.1304 | 31.8546 | 31.9 | 43 | 1.7917 | 1179.1304 | 53330.304
| 44 | 31.8546 | 1177.6283 | 31.7631 | 31.8 | 44 | 1.8333 | 1177.6283 | 54507.9324
| 45 | 31.7631 | 1176.1281 | 31.6717 | 31.7 | 45 | 1.875 | 1176.1281 | 55684.0604
| 46 | 31.6717 | 1174.6298 | 31.5804 | 31.6 | 46 | 1.9167 | 1174.6298 | 56858.6902
| 47 | 31.5804 | 1173.1334 | 31.4892 | 31.5 | 47 | 1.9583 | 1173.1334 | 58031.8237
| 48 | 31.4892 | 1171.6389 | 31.3981 | 31.4 | 48 | 2 | 1171.6389 | 59203.4626
| 49 | 31.3981 | 1170.1463 | 31.3071 | 31.3 | 49 | 2.0417 | 1170.1463 | 60373.6089
| 50 | 31.3071 | 1168.6557 | 31.2163 | 31.2 | 50 | 2.0833 | 1168.6557 | 61542.2646
| 51 | 31.2163 | 1167.1669 | 31.1256 | 31.1 | 51 | 2.125 | 1167.1669 | 62709.4315
| 52 | 31.1256 | 1165.68 | 31.035 | 31 | 52 | 2.1667 | 1165.68 | 63875.1115
| 53 | 31.035 | 1164.195 | 30.9445 | 30.9 | 53 | 2.2083 | 1164.195 | 65039.3065
| 54 | 30.9445 | 1162.7119 | 30.8541 | 30.9 | 54 | 2.25 | 1162.7119 | 66202.0184
| 55 | 30.8541 | 1161.2307 | 30.7638 | 30.8 | 55 | 2.2917 | 1161.2307 | 67363.2491
| 56 | 30.7638 | 1159.7514 | 30.6737 | 30.7 | 56 | 2.3333 | 1159.7514 | 68523.0005
| 57 | 30.6737 | 1158.274 | 30.5837 | 30.6 | 57 | 2.375 | 1158.274 | 69681.2745
| 58 | 30.5837 | 1156.7984 | 30.4937 | 30.5 | 58 | 2.4167 | 1156.7984 | 70838.0729
| 59 | 30.4937 | 1155.3247 | 30.4039 | 30.4 | 59 | 2.4583 | 1155.3247 | 71993.3976
| 60 | 30.4039 | 1153.8529 | 30.3142 | 30.3 | 60 | 2.5 | 1153.8529 | 73147.2505
| 61 | 30.3142 | 1152.383 | 30.2247 | 30.2 | 61 | 2.5417 | 1152.383 | 74299.6335
| 62 | 30.2247 | 1150.915 | 30.1352 | 30.1 | 62 | 2.5833 | 1150.915 | 75450.5485
| 63 | 30.1352 | 1149.4488 | 30.0459 | 30 | 63 | 2.625 | 1149.4488 | 76599.9973
| 64 | 30.0459 | 1147.9845 | 29.9566 | 30 | 64 | 2.6667 | 1147.9845 | 77747.9818
| 65 | 29.9566 | 1146.522 | 29.8675 | 29.9 | 65 | 2.7083 | 1146.522 | 78894.5038
| 66 | 29.8675 | 1145.0614 | 29.7785 | 29.8 | 66 | 2.75 | 1145.0614 | 80039.5652
| 67 | 29.7785 | 1143.6027 | 29.6896 | 29.7 | 67 | 2.7917 | 1143.6027 | 81183.1679
| 68 | 29.6896 | 1142.1459 | 29.6008 | 29.6 | 68 | 2.8333 | 1142.1459 | 82325.3138
| 69 | 29.6008 | 1140.6908 | 29.5122 | 29.5 | 69 | 2.875 | 1140.6908 | 83466.0046
| 70 | 29.5122 | 1139.2377 | 29.4236 | 29.4 | 70 | 2.9167 | 1139.2377 | 84605.2423
| 71 | 29.4236 | 1137.7864 | 29.3352 | 29.3 | 71 | 2.9583 | 1137.7864 | 85743.0287
| 72 | 29.3352 | 1136.3369 | 29.2468 | 29.2 | 72 | 3 | 1136.3369 | 86879.3657
| 73 | 29.2468 | 1134.8893 | 29.1586 | 29.2 | 73 | 3.0417 | 1134.8893 | 88014.255
| 74 | 29.1586 | 1133.4436 | 29.0705 | 29.1 | 74 | 3.0833 | 1133.4436 | 89147.6986
| 75 | 29.0705 | 1131.9996 | 28.9825 | 29 | 75 | 3.125 | 1131.9996 | 90279.6982
| 76 | 28.9825 | 1130.5576 | 28.8947 | 28.9 | 76 | 3.1667 | 1130.5576 | 91410.2558
| 77 | 28.8947 | 1129.1173 | 28.8069 | 28.8 | 77 | 3.2083 | 1129.1173 | 92539.3731
| 78 | 28.8069 | 1127.6789 | 28.7192 | 28.7 | 78 | 3.25 | 1127.6789 | 93667.052
| 79 | 28.7192 | 1126.2423 | 28.6317 | 28.6 | 79 | 3.2917 | 1126.2423 | 94793.2943
| 80 | 28.6317 | 1124.8076 | 28.5443 | 28.5 | 80 | 3.3333 | 1124.8076 | 95918.1019
| 81 | 28.5443 | 1123.3747 | 28.4569 | 28.5 | 81 | 3.375 | 1123.3747 | 97041.4766
| 82 | 28.4569 | 1121.9436 | 28.3697 | 28.4 | 82 | 3.4167 | 1121.9436 | 98163.4201
| 83 | 28.3697 | 1120.5143 | 28.2826 | 28.3 | 83 | 3.4583 | 1120.5143 | 99283.9344
| 84 | 28.2826 | 1119.0868 | 28.1956 | 28.2 | 84 | 3.5 | 1119.0868 | 100403.0213
| 85 | 28.1956 | 1117.6612 | 28.1088 | 28.1 | 85 | 3.5417 | 1117.6612 | 101520.6825
| 86 | 28.1088 | 1116.2374 | 28.022 | 28 | 86 | 3.5833 | 1116.2374 | 102636.9199
| 87 | 28.022 | 1114.8154 | 27.9353 | 27.9 | 87 | 3.625 | 1114.8154 | 103751.7353
| 88 | 27.9353 | 1113.3952 | 27.8488 | 27.8 | 88 | 3.6667 | 1113.3952 | 104865.1305
| 89 | 27.8488 | 1111.9768 | 27.7624 | 27.8 | 89 | 3.7083 | 1111.9768 | 105977.1073
| 90 | 27.7624 | 1110.5602 | 27.676 | 27.7 | 90 | 3.75 | 1110.5602 | 107087.6675
| 91 | 27.676 | 1109.1455 | 27.5898 | 27.6 | 91 | 3.7917 | 1109.1455 | 108196.813
| 92 | 27.5898 | 1107.7325 | 27.5037 | 27.5 | 92 | 3.8333 | 1107.7325 | 109304.5455
| 93 | 27.5037 | 1106.3213 | 27.4177 | 27.4 | 93 | 3.875 | 1106.3213 | 110410.8668
| 94 | 27.4177 | 1104.912 | 27.3318 | 27.3 | 94 | 3.9167 | 1104.912 | 111515.7788
| 95 | 27.3318 | 1103.5044 | 27.2461 | 27.2 | 95 | 3.9583 | 1103.5044 | 112619.2832
| 96 | 27.2461 | 1102.0986 | 27.1604 | 27.2 | 96 | 4 | 1102.0986 | 113721.3818
| 97 | 27.1604 | 1100.6946 | 27.0748 | 27.1 | 97 | 4.0417 | 1100.6946 | 114822.0764
| 98 | 27.0748 | 1099.2924 | 26.9894 | 27 | 98 | 4.0833 | 1099.2924 | 115921.3689
| 99 | 26.9894 | 1097.892 | 26.9041 | 26.9 | 99 | 4.125 | 1097.892 | 117019.2609
| 100 | 26.9041 | 1096.4934 | 26.8188 | 26.8 | 100 | 4.1667 | 1096.4934 | 118115.7542
| 101 | 26.8188 | 1095.0965 | 26.7337 | 26.7 | 101 | 4.2083 | 1095.0965 | 119210.8508
| 102 | 26.7337 | 1093.7015 | 26.6487 | 26.6 | 102 | 4.25 | 1093.7015 | 120304.5522
| 103 | 26.6487 | 1092.3082 | 26.5638 | 26.6 | 103 | 4.2917 | 1092.3082 | 121396.8604
| 104 | 26.5638 | 1090.9166 | 26.479 | 26.5 | 104 | 4.3333 | 1090.9166 | 122487.777
| 105 | 26.479 | 1089.5269 | 26.3943 | 26.4 | 105 | 4.375 | 1089.5269 | 123577.3039
| 106 | 26.3943 | 1088.1389 | 26.3097 | 26.3 | 106 | 4.4167 | 1088.1389 | 124665.4428
| 107 | 26.3097 | 1086.7527 | 26.2252 | 26.2 | 107 | 4.4583 | 1086.7527 | 125752.1955
| 108 | 26.2252 | 1085.3683 | 26.1409 | 26.1 | 108 | 4.5 | 1085.3683 | 126837.5638
| 109 | 26.1409 | 1083.9856 | 26.0566 | 26.1 | 109 | 4.5417 | 1083.9856 | 127921.5494
| 110 | 26.0566 | 1082.6047 | 25.9725 | 26 | 110 | 4.5833 | 1082.6047 | 129004.1541
| 111 | 25.9725 | 1081.2255 | 25.8884 | 25.9 | 111 | 4.625 | 1081.2255 | 130085.3796
| 112 | 25.8884 | 1079.8481 | 25.8045 | 25.8 | 112 | 4.6667 | 1079.8481 | 131165.2277
| 113 | 25.8045 | 1078.4725 | 25.7207 | 25.7 | 113 | 4.7083 | 1078.4725 | 132243.7002
| 114 | 25.7207 | 1077.0986 | 25.6369 | 25.6 | 114 | 4.75 | 1077.0986 | 133320.7988
| 115 | 25.6369 | 1075.7264 | 25.5533 | 25.6 | 115 | 4.7917 | 1075.7264 | 134396.5252
| 116 | 25.5533 | 1074.356 | 25.4698 | 25.5 | 116 | 4.8333 | 1074.356 | 135470.8813
| 117 | 25.4698 | 1072.9874 | 25.3864 | 25.4 | 117 | 4.875 | 1072.9874 | 136543.8687
| 118 | 25.3864 | 1071.6205 | 25.3031 | 25.3 | 118 | 4.9167 | 1071.6205 | 137615.4892
| 119 | 25.3031 | 1070.2553 | 25.2199 | 25.2 | 119 | 4.9583 | 1070.2553 | 138685.7445
| 120 | 25.2199 | 1068.8919 | 25.1368 | 25.1 | 120 | 5 | 1068.8919 | 139754.6364
| 121 | 25.1368 | 1067.5302 | 25.0539 | 25.1 | 121 | 5.0417 | 1067.5302 | 140822.1666
| 122 | 25.0539 | 1066.1703 | 24.971 | 25 | 122 | 5.0833 | 1066.1703 | 141888.3369
| 123 | 24.971 | 1064.812 | 24.8882 | 24.9 | 123 | 5.125 | 1064.812 | 142953.1489
| 124 | 24.8882 | 1063.4556 | 24.8055 | 24.8 | 124 | 5.1667 | 1063.4556 | 144016.6045
| 125 | 24.8055 | 1062.1008 | 24.723 | 24.7 | 125 | 5.2083 | 1062.1008 | 145078.7053
| 126 | 24.723 | 1060.7478 | 24.6405 | 24.6 | 126 | 5.25 | 1060.7478 | 146139.453
| 127 | 24.6405 | 1059.3964 | 24.5582 | 24.6 | 127 | 5.2917 | 1059.3964 | 147198.8495
| 128 | 24.5582 | 1058.0469 | 24.476 | 24.5 | 128 | 5.3333 | 1058.0469 | 148256.8963
| 129 | 24.476 | 1056.699 | 24.3938 | 24.4 | 129 | 5.375 | 1056.699 | 149313.5953
| 130 | 24.3938 | 1055.3528 | 24.3118 | 24.3 | 130 | 5.4167 | 1055.3528 | 150368.9481
| 131 | 24.3118 | 1054.0084 | 24.2299 | 24.2 | 131 | 5.4583 | 1054.0084 | 151422.9565
| 132 | 24.2299 | 1052.6657 | 24.148 | 24.1 | 132 | 5.5 | 1052.6657 | 152475.6222
| 133 | 24.148 | 1051.3246 | 24.0663 | 24.1 | 133 | 5.5417 | 1051.3246 | 153526.9468
| 134 | 24.0663 | 1049.9853 | 23.9847 | 24 | 134 | 5.5833 | 1049.9853 | 154576.9322
| 135 | 23.9847 | 1048.6477 | 23.9032 | 23.9 | 135 | 5.625 | 1048.6477 | 155625.5799
| 136 | 23.9032 | 1047.3118 | 23.8218 | 23.8 | 136 | 5.6667 | 1047.3118 | 156672.8917
| 137 | 23.8218 | 1045.9776 | 23.7405 | 23.7 | 137 | 5.7083 | 1045.9776 | 157718.8694
| 138 | 23.7405 | 1044.6451 | 23.6593 | 23.7 | 138 | 5.75 | 1044.6451 | 158763.5145
| 139 | 23.6593 | 1043.3143 | 23.5782 | 23.6 | 139 | 5.7917 | 1043.3143 | 159806.8288
| 140 | 23.5782 | 1041.9852 | 23.4972 | 23.5 | 140 | 5.8333 | 1041.9852 | 160848.8141
| 141 | 23.4972 | 1040.6578 | 23.4163 | 23.4 | 141 | 5.875 | 1040.6578 | 161889.4719
| 142 | 23.4163 | 1039.3321 | 23.3355 | 23.3 | 142 | 5.9167 | 1039.3321 | 162928.804
| 143 | 23.3355 | 1038.0081 | 23.2548 | 23.3 | 143 | 5.9583 | 1038.0081 | 163966.8121
| 144 | 23.2548 | 1036.6857 | 23.1742 | 23.2 | 144 | 6 | 1036.6857 | 165003.4978
| 145 | 23.1742 | 1035.3651 | 23.0938 | 23.1 | 145 | 6.0417 | 1035.3651 | 166038.8629
| 146 | 23.0938 | 1034.0461 | 23.0134 | 23 | 146 | 6.0833 | 1034.0461 | 167072.909
| 147 | 23.0134 | 1032.7288 | 22.9331 | 22.9 | 147 | 6.125 | 1032.7288 | 168105.6378
| 148 | 22.9331 | 1031.4132 | 22.8529 | 22.9 | 148 | 6.1667 | 1031.4132 | 169137.0509
| 149 | 22.8529 | 1030.0992 | 22.7729 | 22.8 | 149 | 6.2083 | 1030.0992 | 170167.1502
| 150 | 22.7729 | 1028.787 | 22.6929 | 22.7 | 150 | 6.25 | 1028.787 | 171195.9371
| 151 | 22.6929 | 1027.4764 | 22.613 | 22.6 | 151 | 6.2917 | 1027.4764 | 172223.4135
| 152 | 22.613 | 1026.1674 | 22.5333 | 22.5 | 152 | 6.3333 | 1026.1674 | 173249.581
| 153 | 22.5333 | 1024.8602 | 22.4536 | 22.5 | 153 | 6.375 | 1024.8602 | 174274.4411
| 154 | 22.4536 | 1023.5546 | 22.374 | 22.4 | 154 | 6.4167 | 1023.5546 | 175297.9957
| 155 | 22.374 | 1022.2507 | 22.2946 | 22.3 | 155 | 6.4583 | 1022.2507 | 176320.2464
| 156 | 22.2946 | 1020.9484 | 22.2152 | 22.2 | 156 | 6.5 | 1020.9484 | 177341.1948
| 157 | 22.2152 | 1019.6478 | 22.136 | 22.1 | 157 | 6.5417 | 1019.6478 | 178360.8425
| 158 | 22.136 | 1018.3488 | 22.0568 | 22.1 | 158 | 6.5833 | 1018.3488 | 179379.1914
| 159 | 22.0568 | 1017.0515 | 21.9778 | 22 | 159 | 6.625 | 1017.0515 | 180396.2429
| 160 | 21.9778 | 1015.7559 | 21.8988 | 21.9 | 160 | 6.6667 | 1015.7559 | 181411.9988
| 161 | 21.8988 | 1014.4619 | 21.8199 | 21.8 | 161 | 6.7083 | 1014.4619 | 182426.4606
| 162 | 21.8199 | 1013.1695 | 21.7412 | 21.7 | 162 | 6.75 | 1013.1695 | 183439.6302
| 163 | 21.7412 | 1011.8788 | 21.6625 | 21.7 | 163 | 6.7917 | 1011.8788 | 184451.509
| 164 | 21.6625 | 1010.5898 | 21.584 | 21.6 | 164 | 6.8333 | 1010.5898 | 185462.0988
| 165 | 21.584 | 1009.3024 | 21.5055 | 21.5 | 165 | 6.875 | 1009.3024 | 186471.4011
40 | 166 | 21.5055 | 1008.0166 | 21.4272 | 21.4 | 166 | 6.9167 | 1008.0166 | 187479.4177
#N/A | 167 | 21.4272 | 1006.7324 | 21.3489 | 21.3 | 167 | 6.9583 | 1006.7324 | 188486.1501
41 | 168 | 21.3489 | 1005.4499 | 21.2708 | 21.3 | 168 | 7 | 1005.4499 | 189491.6001
| 169 | 21.2708 | 1004.1691 | 21.1927 | 21.2 | 169 | 7.0417 | 1004.1691 | 190495.7691
| 170 | 21.1927 | 1002.8898 | 21.1148 | 21.1 | 170 | 7.0833 | 1002.8898 | 191498.659
| 171 | 21.1148 | 1001.6122 | 21.0369 | 21 | 171 | 7.125 | 1001.6122 | 192500.2712
| 172 | 21.0369 | 1000.3363 | 20.9591 | 21 | 172 | 7.1667 | 1000.3363 | 193500.6075
| 173 | 20.9591 | 999.0619 | 20.8815 | 20.9 | 173 | 7.2083 | 999.0619 | 194499.6694
| 174 | 20.8815 | 997.7892 | 20.8039 | 20.8 | 174 | 7.25 | 997.7892 | 195497.4585
| 175 | 20.8039 | 996.5181 | 20.7265 | 20.7 | 175 | 7.2917 | 996.5181 | 196493.9766
| 176 | 20.7265 | 995.2486 | 20.6491 | 20.6 | 176 | 7.3333 | 995.2486 | 197489.2252
| 177 | 20.6491 | 993.9807 | 20.5718 | 20.6 | 177 | 7.375 | 993.9807 | 198483.2059
| 178 | 20.5718 | 992.7144 | 20.4947 | 20.5 | 178 | 7.4167 | 992.7144 | 199475.9203
| 179 | 20.4947 | 991.4498 | 20.4176 | 20.4 | 179 | 7.4583 | 991.4498 | 200467.3701
| 180 | 20.4176 | 990.1868 | 20.3406 | 20.3 | 180 | 7.5 | 990.1868 | 201457.5569
| 181 | 20.3406 | 988.9253 | 20.2638 | 20.3 | 181 | 7.5417 | 988.9253 | 202446.4822
| 182 | 20.2638 | 987.6655 | 20.187 | 20.2 | 182 | 7.5833 | 987.6655 | 203434.1478
| 183 | 20.187 | 986.4073 | 20.1103 | 20.1 | 183 | 7.625 | 986.4073 | 204420.5551
| 184 | 20.1103 | 985.1507 | 20.0338 | 20 | 184 | 7.6667 | 985.1507 | 205405.7058
| 185 | 20.0338 | 983.8957 | 19.9573 | 20 | 185 | 7.7083 | 983.8957 | 206389.6015
| 186 | 19.9573 | 982.6423 | 19.8809 | 19.9 | 186 | 7.75 | 982.6423 | 207372.2438
| 187 | 19.8809 | 981.3905 | 19.8046 | 19.8 | 187 | 7.7917 | 981.3905 | 208353.6343
| 188 | 19.8046 | 980.1403 | 19.7284 | 19.7 | 188 | 7.8333 | 980.1403 | 209333.7745
| 189 | 19.7284 | 978.8916 | 19.6523 | 19.7 | 189 | 7.875 | 978.8916 | 210312.6662
| 190 | 19.6523 | 977.6446 | 19.5763 | 19.6 | 190 | 7.9167 | 977.6446 | 211290.3108
| 191 | 19.5763 | 976.3992 | 19.5005 | 19.5 | 191 | 7.9583 | 976.3992 | 212266.7099
| 192 | 19.5005 | 975.1553 | 19.4247 | 19.4 | 192 | 8 | 975.1553 | 213241.8652
| 193 | 19.4247 | 973.913 | 19.3489 | 19.3 | 193 | 8.0417 | 973.913 | 214215.7783
| 194 | 19.3489 | 972.6723 | 19.2733 | 19.3 | 194 | 8.0833 | 972.6723 | 215188.4506
| 195 | 19.2733 | 971.4332 | 19.1978 | 19.2 | 195 | 8.125 | 971.4332 | 216159.8838
| 196 | 19.1978 | 970.1957 | 19.1224 | 19.1 | 196 | 8.1667 | 970.1957 | 217130.0795
| 197 | 19.1224 | 968.9597 | 19.0471 | 19 | 197 | 8.2083 | 968.9597 | 218099.0392
| 198 | 19.0471 | 967.7254 | 18.9719 | 19 | 198 | 8.25 | 967.7254 | 219066.7646
| 199 | 18.9719 | 966.4925 | 18.8968 | 18.9 | 199 | 8.2917 | 966.4925 | 220033.2571
| 200 | 18.8968 | 965.2613 | 18.8217 | 18.8 | 200 | 8.3333 | 965.2613 | 220998.5184
| 201 | 18.8217 | 964.0316 | 18.7468 | 18.7 | 201 | 8.375 | 964.0316 | 221962.5501
| 202 | 18.7468 | 962.8035 | 18.672 | 18.7 | 202 | 8.4167 | 962.8035 | 222925.3536
| 203 | 18.672 | 961.577 | 18.5972 | 18.6 | 203 | 8.4583 | 961.577 | 223886.9306
| 204 | 18.5972 | 960.352 | 18.5226 | 18.5 | 204 | 8.5 | 960.352 | 224847.2826
| 205 | 18.5226 | 959.1286 | 18.448 | 18.4 | 205 | 8.5417 | 959.1286 | 225806.4112
| 206 | 18.448 | 957.9067 | 18.3735 | 18.4 | 206 | 8.5833 | 957.9067 | 226764.3179
| 207 | 18.3735 | 956.6864 | 18.2992 | 18.3 | 207 | 8.625 | 956.6864 | 227721.0044
| 208 | 18.2992 | 955.4677 | 18.2249 | 18.2 | 208 | 8.6667 | 955.4677 | 228676.4721
| 209 | 18.2249 | 954.2505 | 18.1507 | 18.2 | 209 | 8.7083 | 954.2505 | 229630.7226
| 210 | 18.1507 | 953.0349 | 18.0767 | 18.1 | 210 | 8.75 | 953.0349 | 230583.7574
| 211 | 18.0767 | 951.8208 | 18.0027 | 18 | 211 | 8.7917 | 951.8208 | 231535.5782
| 212 | 18.0027 | 950.6082 | 17.9288 | 17.9 | 212 | 8.8333 | 950.6082 | 232486.1864
| 213 | 17.9288 | 949.3972 | 17.855 | 17.9 | 213 | 8.875 | 949.3972 | 233435.5836
| 214 | 17.855 | 948.1877 | 17.7813 | 17.8 | 214 | 8.9167 | 948.1877 | 234383.7714
| 215 | 17.7813 | 946.9798 | 17.7077 | 17.7 | 215 | 8.9583 | 946.9798 | 235330.7512
| 216 | 17.7077 | 945.7734 | 17.6342 | 17.6 | 216 | 9 | 945.7734 | 236276.5246
| 217 | 17.6342 | 944.5686 | 17.5607 | 17.6 | 217 | 9.0417 | 944.5686 | 237221.0932
| 218 | 17.5607 | 943.3653 | 17.4874 | 17.5 | 218 | 9.0833 | 943.3653 | 238164.4585
| 219 | 17.4874 | 942.1635 | 17.4142 | 17.4 | 219 | 9.125 | 942.1635 | 239106.6221
| 220 | 17.4142 | 940.9633 | 17.341 | 17.3 | 220 | 9.1667 | 940.9633 | 240047.5853
| 221 | 17.341 | 939.7646 | 17.268 | 17.3 | 221 | 9.2083 | 939.7646 | 240987.3499
| 222 | 17.268 | 938.5674 | 17.195 | 17.2 | 222 | 9.25 | 938.5674 | 241925.9173
| 223 | 17.195 | 937.3717 | 17.1222 | 17.1 | 223 | 9.2917 | 937.3717 | 242863.289
| 224 | 17.1222 | 936.1776 | 17.0494 | 17 | 224 | 9.3333 | 936.1776 | 243799.4665
| 225 | 17.0494 | 934.9849 | 16.9767 | 17 | 225 | 9.375 | 934.9849 | 244734.4515
| 226 | 16.9767 | 933.7938 | 16.9041 | 16.9 | 226 | 9.4167 | 933.7938 | 245668.2453
| 227 | 16.9041 | 932.6043 | 16.8316 | 16.8 | 227 | 9.4583 | 932.6043 | 246600.8496
| 228 | 16.8316 | 931.4162 | 16.7592 | 16.8 | 228 | 9.5 | 931.4162 | 247532.2658
| 229 | 16.7592 | 930.2296 | 16.6869 | 16.7 | 229 | 9.5417 | 930.2296 | 248462.4954
| 230 | 16.6869 | 929.0446 | 16.6147 | 16.6 | 230 | 9.5833 | 929.0446 | 249391.54
| 231 | 16.6147 | 927.8611 | 16.5426 | 16.5 | 231 | 9.625 | 927.8611 | 250319.4011
| 232 | 16.5426 | 926.679 | 16.4706 | 16.5 | 232 | 9.6667 | 926.679 | 251246.0801
| 233 | 16.4706 | 925.4985 | 16.3986 | 16.4 | 233 | 9.7083 | 925.4985 | 252171.5786
| 234 | 16.3986 | 924.3195 | 16.3268 | 16.3 | 234 | 9.75 | 924.3195 | 253095.8981
| 235 | 16.3268 | 923.142 | 16.255 | 16.3 | 235 | 9.7917 | 923.142 | 254019.0401
| 236 | 16.255 | 921.966 | 16.1834 | 16.2 | 236 | 9.8333 | 921.966 | 254941.0061
| 237 | 16.1834 | 920.7915 | 16.1118 | 16.1 | 237 | 9.875 | 920.7915 | 255861.7975
| 238 | 16.1118 | 919.6184 | 16.0403 | 16 | 238 | 9.9167 | 919.6184 | 256781.416
| 239 | 16.0403 | 918.4469 | 15.9689 | 16 | 239 | 9.9583 | 918.4469 | 257699.8629
| 240 | 15.9689 | 917.2769 | 15.8976 | 15.9 | 240 | 10 | 917.2769 | 258617.1398
| 241 | 15.8976 | 916.1083 | 15.8264 | 15.8 | 241 | 10.0417 | 916.1083 | 259533.2481
| 242 | 15.8264 | 914.9413 | 15.7553 | 15.8 | 242 | 10.0833 | 914.9413 | 260448.1894
| 243 | 15.7553 | 913.7757 | 15.6843 | 15.7 | 243 | 10.125 | 913.7757 | 261361.9651
| 244 | 15.6843 | 912.6116 | 15.6133 | 15.6 | 244 | 10.1667 | 912.6116 | 262274.5768
| 245 | 15.6133 | 911.449 | 15.5425 | 15.5 | 245 | 10.2083 | 911.449 | 263186.0258
| 246 | 15.5425 | 910.2879 | 15.4717 | 15.5 | 246 | 10.25 | 910.2879 | 264096.3138
| 247 | 15.4717 | 909.1283 | 15.4011 | 15.4 | 247 | 10.2917 | 909.1283 | 265005.442
| 248 | 15.4011 | 907.9701 | 15.3305 | 15.3 | 248 | 10.3333 | 907.9701 | 265913.4122
| 249 | 15.3305 | 906.8134 | 15.26 | 15.3 | 249 | 10.375 | 906.8134 | 266820.2256
| 250 | 15.26 | 905.6582 | 15.1896 | 15.2 | 250 | 10.4167 | 905.6582 | 267725.8838
| 251 | 15.1896 | 904.5045 | 15.1193 | 15.1 | 251 | 10.4583 | 904.5045 | 268630.3883
| 252 | 15.1193 | 903.3522 | 15.0491 | 15 | 252 | 10.5 | 903.3522 | 269533.7406
| 253 | 15.0491 | 902.2014 | 14.9789 | 15 | 253 | 10.5417 | 902.2014 | 270435.942
| 254 | 14.9789 | 901.0521 | 14.9089 | 14.9 | 254 | 10.5833 | 901.0521 | 271336.9941
| 255 | 14.9089 | 899.9042 | 14.839 | 14.8 | 255 | 10.625 | 899.9042 | 272236.8983
| 256 | 14.839 | 898.7578 | 14.7691 | 14.8 | 256 | 10.6667 | 898.7578 | 273135.6561
| 257 | 14.7691 | 897.6128 | 14.6993 | 14.7 | 257 | 10.7083 | 897.6128 | 274033.2689
| 258 | 14.6993 | 896.4694 | 14.6296 | 14.6 | 258 | 10.75 | 896.4694 | 274929.7383
| 259 | 14.6296 | 895.3273 | 14.56 | 14.6 | 259 | 10.7917 | 895.3273 | 275825.0656
| 260 | 14.56 | 894.1867 | 14.4905 | 14.5 | 260 | 10.8333 | 894.1867 | 276719.2523
| 261 | 14.4905 | 893.0476 | 14.4211 | 14.4 | 261 | 10.875 | 893.0476 | 277612.2999
| 262 | 14.4211 | 891.9099 | 14.3518 | 14.4 | 262 | 10.9167 | 891.9099 | 278504.2099
| 263 | 14.3518 | 890.7737 | 14.2826 | 14.3 | 263 | 10.9583 | 890.7737 | 279394.9836
| 264 | 14.2826 | 889.6389 | 14.2134 | 14.2 | 264 | 11 | 889.6389 | 280284.6225
| 265 | 14.2134 | 888.5056 | 14.1443 | 14.1 | 265 | 11.0417 | 888.5056 | 281173.1281
| 266 | 14.1443 | 887.3737 | 14.0754 | 14.1 | 266 | 11.0833 | 887.3737 | 282060.5019
| 267 | 14.0754 | 886.2433 | 14.0065 | 14 | 267 | 11.125 | 886.2433 | 282946.7451
| 268 | 14.0065 | 885.1143 | 13.9377 | 13.9 | 268 | 11.1667 | 885.1143 | 283831.8594
| 269 | 13.9377 | 883.9867 | 13.869 | 13.9 | 269 | 11.2083 | 883.9867 | 284715.8461
| 270 | 13.869 | 882.8606 | 13.8003 | 13.8 | 270 | 11.25 | 882.8606 | 285598.7066
| 271 | 13.8003 | 881.7359 | 13.7318 | 13.7 | 271 | 11.2917 | 881.7359 | 286480.4425
| 272 | 13.7318 | 880.6126 | 13.6633 | 13.7 | 272 | 11.3333 | 880.6126 | 287361.0551
| 273 | 13.6633 | 879.4908 | 13.595 | 13.6 | 273 | 11.375 | 879.4908 | 288240.5459
| 274 | 13.595 | 878.3704 | 13.5267 | 13.5 | 274 | 11.4167 | 878.3704 | 289118.9162
| 275 | 13.5267 | 877.2514 | 13.4585 | 13.5 | 275 | 11.4583 | 877.2514 | 289996.1676
| 276 | 13.4585 | 876.1338 | 13.3904 | 13.4 | 276 | 11.5 | 876.1338 | 290872.3014
| 277 | 13.3904 | 875.0177 | 13.3224 | 13.3 | 277 | 11.5417 | 875.0177 | 291747.3191
| 278 | 13.3224 | 873.903 | 13.2545 | 13.3 | 278 | 11.5833 | 873.903 | 292621.2221
| 279 | 13.2545 | 872.7897 | 13.1866 | 13.2 | 279 | 11.625 | 872.7897 | 293494.0118
| 280 | 13.1866 | 871.6778 | 13.1189 | 13.1 | 280 | 11.6667 | 871.6778 | 294365.6896
| 281 | 13.1189 | 870.5674 | 13.0512 | 13.1 | 281 | 11.7083 | 870.5674 | 295236.257
| 282 | 13.0512 | 869.4583 | 12.9836 | 13 | 282 | 11.75 | 869.4583 | 296105.7154
| 283 | 12.9836 | 868.3507 | 12.9161 | 12.9 | 283 | 11.7917 | 868.3507 | 296974.0661
| 284 | 12.9161 | 867.2445 | 12.8487 | 12.8 | 284 | 11.8333 | 867.2445 | 297841.3106
| 285 | 12.8487 | 866.1397 | 12.7814 | 12.8 | 285 | 11.875 | 866.1397 | 298707.4503
| 286 | 12.7814 | 865.0363 | 12.7141 | 12.7 | 286 | 11.9167 | 865.0363 | 299572.4866
| 287 | 12.7141 | 863.9343 | 12.647 | 12.6 | 287 | 11.9583 | 863.9343 | 300436.4209
| 288 | 12.647 | 862.8337 | 12.5799 | 12.6 | 288 | 12 | 862.8337 | 301299.2547
| 289 | 12.5799 | 861.7345 | 12.5129 | 12.5 | 289 | 12.0417 | 861.7345 | 302160.9892
| 290 | 12.5129 | 860.6368 | 12.446 | 12.4 | 290 | 12.0833 | 860.6368 | 303021.626
| 291 | 12.446 | 859.5404 | 12.3792 | 12.4 | 291 | 12.125 | 859.5404 | 303881.1663
| 292 | 12.3792 | 858.4454 | 12.3125 | 12.3 | 292 | 12.1667 | 858.4454 | 304739.6117
| 293 | 12.3125 | 857.3518 | 12.2459 | 12.2 | 293 | 12.2083 | 857.3518 | 305596.9635
| 294 | 12.2459 | 856.2596 | 12.1793 | 12.2 | 294 | 12.25 | 856.2596 | 306453.2231
| 295 | 12.1793 | 855.1688 | 12.1128 | 12.1 | 295 | 12.2917 | 855.1688 | 307308.3919
| 296 | 12.1128 | 854.0794 | 12.0464 | 12 | 296 | 12.3333 | 854.0794 | 308162.4712
| 297 | 12.0464 | 852.9913 | 11.9801 | 12 | 297 | 12.375 | 852.9913 | 309015.4626
| 298 | 11.9801 | 851.9047 | 11.9139 | 11.9 | 298 | 12.4167 | 851.9047 | 309867.3672
| 299 | 11.9139 | 850.8194 | 11.8478 | 11.8 | 299 | 12.4583 | 850.8194 | 310718.1867
| 300 | 11.8478 | 849.7355 | 11.7817 | 11.8 | 300 | 12.5 | 849.7355 | 311567.9222
| 301 | 11.7817 | 848.653 | 11.7158 | 11.7 | 301 | 12.5417 | 848.653 | 312416.5752
| 302 | 11.7158 | 847.5719 | 11.6499 | 11.6 | 302 | 12.5833 | 847.5719 | 313264.1472
| 303 | 11.6499 | 846.4922 | 11.5841 | 11.6 | 303 | 12.625 | 846.4922 | 314110.6393
| 304 | 11.5841 | 845.4138 | 11.5184 | 11.5 | 304 | 12.6667 | 845.4138 | 314956.0531
| 305 | 11.5184 | 844.3368 | 11.4527 | 11.5 | 305 | 12.7083 | 844.3368 | 315800.3899
| 306 | 11.4527 | 843.2612 | 11.3872 | 11.4 | 306 | 12.75 | 843.2612 | 316643.6511
| 307 | 11.3872 | 842.1869 | 11.3217 | 11.3 | 307 | 12.7917 | 842.1869 | 317485.8381
| 308 | 11.3217 | 841.1141 | 11.2564 | 11.3 | 308 | 12.8333 | 841.1141 | 318326.9521
| 309 | 11.2564 | 840.0425 | 11.1911 | 11.2 | 309 | 12.875 | 840.0425 | 319166.9947
| 310 | 11.1911 | 838.9724 | 11.1258 | 11.1 | 310 | 12.9167 | 838.9724 | 320005.9671
| 311 | 11.1258 | 837.9036 | 11.0607 | 11.1 | 311 | 12.9583 | 837.9036 | 320843.8707
| 312 | 11.0607 | 836.8362 | 10.9957 | 11 | 312 | 13 | 836.8362 | 321680.7068
| 313 | 10.9957 | 835.7701 | 10.9307 | 10.9 | 313 | 13.0417 | 835.7701 | 322516.477
| 314 | 10.9307 | 834.7054 | 10.8658 | 10.9 | 314 | 13.0833 | 834.7054 | 323351.1824
| 315 | 10.8658 | 833.6421 | 10.801 | 10.8 | 315 | 13.125 | 833.6421 | 324184.8244
| 316 | 10.801 | 832.5801 | 10.7363 | 10.7 | 316 | 13.1667 | 832.5801 | 325017.4045
| 317 | 10.7363 | 831.5194 | 10.6717 | 10.7 | 317 | 13.2083 | 831.5194 | 325848.9239
| 318 | 10.6717 | 830.4601 | 10.6071 | 10.6 | 318 | 13.25 | 830.4601 | 326679.384
| 319 | 10.6071 | 829.4022 | 10.5427 | 10.5 | 319 | 13.2917 | 829.4022 | 327508.7862
| 320 | 10.5427 | 828.3456 | 10.4783 | 10.5 | 320 | 13.3333 | 828.3456 | 328337.1317
| 321 | 10.4783 | 827.2903 | 10.414 | 10.4 | 321 | 13.375 | 827.2903 | 329164.4221
| 322 | 10.414 | 826.2364 | 10.3497 | 10.3 | 322 | 13.4167 | 826.2364 | 329990.6585
| 323 | 10.3497 | 825.1839 | 10.2856 | 10.3 | 323 | 13.4583 | 825.1839 | 330815.8423
| 324 | 10.2856 | 824.1326 | 10.2215 | 10.2 | 324 | 13.5 | 824.1326 | 331639.975
| 325 | 10.2215 | 823.0828 | 10.1576 | 10.2 | 325 | 13.5417 | 823.0828 | 332463.0577
| 326 | 10.1576 | 822.0342 | 10.0937 | 10.1 | 326 | 13.5833 | 822.0342 | 333285.0919
| 327 | 10.0937 | 820.987 | 10.0298 | 10 | 327 | 13.625 | 820.987 | 334106.0789
| 328 | 10.0298 | 819.9411 | 9.9661 | 10 | 328 | 13.6667 | 819.9411 | 334926.0201
| 329 | 9.9661 | 818.8966 | 9.9025 | 9.9 | 329 | 13.7083 | 818.8966 | 335744.9166
| 330 | 9.9025 | 817.8534 | 9.8389 | 9.8 | 330 | 13.75 | 817.8534 | 336562.77
| 331 | 9.8389 | 816.8115 | 9.7754 | 9.8 | 331 | 13.7917 | 816.8115 | 337379.5815
| 332 | 9.7754 | 815.7709 | 9.712 | 9.7 | 332 | 13.8333 | 815.7709 | 338195.3524
| 333 | 9.712 | 814.7317 | 9.6487 | 9.6 | 333 | 13.875 | 814.7317 | 339010.0841
| 334 | 9.6487 | 813.6938 | 9.5854 | 9.6 | 334 | 13.9167 | 813.6938 | 339823.7779
| 335 | 9.5854 | 812.6572 | 9.5222 | 9.5 | 335 | 13.9583 | 812.6572 | 340636.4351
| 336 | 9.5222 | 811.6219 | 9.4591 | 9.5 | 336 | 14 | 811.6219 | 341448.0571
| 337 | 9.4591 | 810.588 | 9.3961 | 9.4 | 337 | 14.0417 | 810.588 | 342258.6451
| 338 | 9.3961 | 809.5554 | 9.3332 | 9.3 | 338 | 14.0833 | 809.5554 | 343068.2004
| 339 | 9.3332 | 808.5241 | 9.2704 | 9.3 | 339 | 14.125 | 808.5241 | 343876.7245
| 340 | 9.2704 | 807.4941 | 9.2076 | 9.2 | 340 | 14.1667 | 807.4941 | 344684.2185
| 341 | 9.2076 | 806.4654 | 9.1449 | 9.1 | 341 | 14.2083 | 806.4654 | 345490.6839
| 342 | 9.1449 | 805.438 | 9.0823 | 9.1 | 342 | 14.25 | 805.438 | 346296.1219
| 343 | 9.0823 | 804.4119 | 9.0198 | 9 | 343 | 14.2917 | 804.4119 | 347100.5338
| 344 | 9.0198 | 803.3872 | 8.9573 | 9 | 344 | 14.3333 | 803.3872 | 347903.921
| 345 | 8.9573 | 802.3637 | 8.895 | 8.9 | 345 | 14.375 | 802.3637 | 348706.2847
| 346 | 8.895 | 801.3416 | 8.8327 | 8.8 | 346 | 14.4167 | 801.3416 | 349507.6263
| 347 | 8.8327 | 800.3207 | 8.7705 | 8.8 | 347 | 14.4583 | 800.3207 | 350307.947
| 348 | 8.7705 | 799.3012 | 8.7083 | 8.7 | 348 | 14.5 | 799.3012 | 351107.2481
| 349 | 8.7083 | 798.2829 | 8.6463 | 8.6 | 349 | 14.5417 | 798.2829 | 351905.5311
| 350 | 8.6463 | 797.266 | 8.5843 | 8.6 | 350 | 14.5833 | 797.266 | 352702.797
| 351 | 8.5843 | 796.2503 | 8.5224 | 8.5 | 351 | 14.625 | 796.2503 | 353499.0473
| 352 | 8.5224 | 795.2359 | 8.4606 | 8.5 | 352 | 14.6667 | 795.2359 | 354294.2833
| 353 | 8.4606 | 794.2229 | 8.3989 | 8.4 | 353 | 14.7083 | 794.2229 | 355088.5061
| 354 | 8.3989 | 793.2111 | 8.3372 | 8.3 | 354 | 14.75 | 793.2111 | 355881.7172
| 355 | 8.3372 | 792.2006 | 8.2756 | 8.3 | 355 | 14.7917 | 792.2006 | 356673.9178
| 356 | 8.2756 | 791.1914 | 8.2141 | 8.2 | 356 | 14.8333 | 791.1914 | 357465.1092
| 357 | 8.2141 | 790.1835 | 8.1527 | 8.2 | 357 | 14.875 | 790.1835 | 358255.2927
| 358 | 8.1527 | 789.1768 | 8.0914 | 8.1 | 358 | 14.9167 | 789.1768 | 359044.4695
| 359 | 8.0914 | 788.1715 | 8.0301 | 8 | 359 | 14.9583 | 788.1715 | 359832.641
| 360 | 8.0301 | 787.1674 | 7.9689 | 8 | 360 | 15 | 787.1674 | 360619.8085
| 361 | 7.9689 | 786.1646 | 7.9078 | 7.9 | 361 | 15.0417 | 786.1646 | 361405.9731
| 362 | 7.9078 | 785.1631 | 7.8468 | 7.8 | 362 | 15.0833 | 785.1631 | 362191.1362
| 363 | 7.8468 | 784.1629 | 7.7858 | 7.8 | 363 | 15.125 | 784.1629 | 362975.2991
| 364 | 7.7858 | 783.1639 | 7.725 | 7.7 | 364 | 15.1667 | 783.1639 | 363758.463
| 365 | 7.725 | 782.1662 | 7.6642 | 7.7 | 365 | 15.2083 | 782.1662 | 364540.6292
| 366 | 7.6642 | 781.1698 | 7.6034 | 7.6 | 366 | 15.25 | 781.1698 | 365321.799
| 367 | 7.6034 | 780.1746 | 7.5428 | 7.5 | 367 | 15.2917 | 780.1746 | 366101.9737
| 368 | 7.5428 | 779.1808 | 7.4822 | 7.5 | 368 | 15.3333 | 779.1808 | 366881.1544
| 369 | 7.4822 | 778.1881 | 7.4217 | 7.4 | 369 | 15.375 | 778.1881 | 367659.3426
| 370 | 7.4217 | 777.1968 | 7.3613 | 7.4 | 370 | 15.4167 | 777.1968 | 368436.5394
| 371 | 7.3613 | 776.2067 | 7.301 | 7.3 | 371 | 15.4583 | 776.2067 | 369212.7461
| 372 | 7.301 | 775.2179 | 7.2407 | 7.2 | 372 | 15.5 | 775.2179 | 369987.9639
| 373 | 7.2407 | 774.2303 | 7.1806 | 7.2 | 373 | 15.5417 | 774.2303 | 370762.1942
| 374 | 7.1806 | 773.244 | 7.1204 | 7.1 | 374 | 15.5833 | 773.244 | 371535.4382
| 375 | 7.1204 | 772.2589 | 7.0604 | 7.1 | 375 | 15.625 | 772.2589 | 372307.6972
| 376 | 7.0604 | 771.2751 | 7.0005 | 7 | 376 | 15.6667 | 771.2751 | 373078.9723
| 377 | 7.0005 | 770.2926 | 6.9406 | 6.9 | 377 | 15.7083 | 770.2926 | 373849.2649
| 378 | 6.9406 | 769.3113 | 6.8808 | 6.9 | 378 | 15.75 | 769.3113 | 374618.5762
| 379 | 6.8808 | 768.3313 | 6.8211 | 6.8 | 379 | 15.7917 | 768.3313 | 375386.9075
| 380 | 6.8211 | 767.3525 | 6.7614 | 6.8 | 380 | 15.8333 | 767.3525 | 376154.2599
| 381 | 6.7614 | 766.3749 | 6.7019 | 6.7 | 381 | 15.875 | 766.3749 | 376920.6348
| 382 | 6.7019 | 765.3986 | 6.6424 | 6.6 | 382 | 15.9167 | 765.3986 | 377686.0334
| 383 | 6.6424 | 764.4235 | 6.5829 | 6.6 | 383 | 15.9583 | 764.4235 | 378450.457
| 384 | 6.5829 | 763.4497 | 6.5236 | 6.5 | 384 | 16 | 763.4497 | 379213.9067
| 385 | 6.5236 | 762.4771 | 6.4643 | 6.5 | 385 | 16.0417 | 762.4771 | 379976.3838
| 386 | 6.4643 | 761.5058 | 6.4051 | 6.4 | 386 | 16.0833 | 761.5058 | 380737.8897
| 387 | 6.4051 | 760.5357 | 6.346 | 6.3 | 387 | 16.125 | 760.5357 | 381498.4254
| 388 | 6.346 | 759.5668 | 6.287 | 6.3 | 388 | 16.1667 | 759.5668 | 382257.9922
| 389 | 6.287 | 758.5992 | 6.228 | 6.2 | 389 | 16.2083 | 758.5992 | 383016.5914
| 390 | 6.228 | 757.6328 | 6.1691 | 6.2 | 390 | 16.25 | 757.6328 | 383774.2242
| 391 | 6.1691 | 756.6676 | 6.1103 | 6.1 | 391 | 16.2917 | 756.6676 | 384530.8919
| 392 | 6.1103 | 755.7037 | 6.0516 | 6.1 | 392 | 16.3333 | 755.7037 | 385286.5956
| 393 | 6.0516 | 754.741 | 5.9929 | 6 | 393 | 16.375 | 754.741 | 386041.3366
| 394 | 5.9929 | 753.7795 | 5.9343 | 5.9 | 394 | 16.4167 | 753.7795 | 386795.1161
| 395 | 5.9343 | 752.8193 | 5.8758 | 5.9 | 395 | 16.4583 | 752.8193 | 387547.9354
| 396 | 5.8758 | 751.8602 | 5.8173 | 5.8 | 396 | 16.5 | 751.8602 | 388299.7956
| 397 | 5.8173 | 750.9024 | 5.759 | 5.8 | 397 | 16.5417 | 750.9024 | 389050.698
| 398 | 5.759 | 749.9458 | 5.7007 | 5.7 | 398 | 16.5833 | 749.9458 | 389800.6438
| 399 | 5.7007 | 748.9904 | 5.6425 | 5.6 | 399 | 16.625 | 748.9904 | 390549.6343
| 400 | 5.6425 | 748.0363 | 5.5843 | 5.6 | 400 | 16.6667 | 748.0363 | 391297.6706
| 401 | 5.5843 | 747.0833 | 5.5263 | 5.5 | 401 | 16.7083 | 747.0833 | 392044.7539
| 402 | 5.5263 | 746.1316 | 5.4683 | 5.5 | 402 | 16.75 | 746.1316 | 392790.8855
| 403 | 5.4683 | 745.1811 | 5.4103 | 5.4 | 403 | 16.7917 | 745.1811 | 393536.0666
| 404 | 5.4103 | 744.2318 | 5.3525 | 5.4 | 404 | 16.8333 | 744.2318 | 394280.2984
| 405 | 5.3525 | 743.2837 | 5.2947 | 5.3 | 405 | 16.875 | 743.2837 | 395023.5821
| 406 | 5.2947 | 742.3368 | 5.237 | 5.2 | 406 | 16.9167 | 742.3368 | 395765.9189
| 407 | 5.237 | 741.3911 | 5.1794 | 5.2 | 407 | 16.9583 | 741.3911 | 396507.3101
| 408 | 5.1794 | 740.4467 | 5.1218 | 5.1 | 408 | 17 | 740.4467 | 397247.7567
| 409 | 5.1218 | 739.5034 | 5.0643 | 5.1 | 409 | 17.0417 | 739.5034 | 397987.2601
| 410 | 5.0643 | 738.5613 | 5.0069 | 5 | 410 | 17.0833 | 738.5613 | 398725.8214
| 411 | 5.0069 | 737.6204 | 4.9496 | 4.9 | 411 | 17.125 | 737.6204 | 399463.4418
| 412 | 4.9496 | 736.6808 | 4.8923 | 4.9 | 412 | 17.1667 | 736.6808 | 400200.1226
| 413 | 4.8923 | 735.7423 | 4.8351 | 4.8 | 413 | 17.2083 | 735.7423 | 400935.8649
| 414 | 4.8351 | 734.805 | 4.778 | 4.8 | 414 | 17.25 | 734.805 | 401670.6699
| 415 | 4.778 | 733.8689 | 4.721 | 4.7 | 415 | 17.2917 | 733.8689 | 402404.5388
| 416 | 4.721 | 732.934 | 4.664 | 4.7 | 416 | 17.3333 | 732.934 | 403137.4729
| 417 | 4.664 | 732.0003 | 4.6071 | 4.6 | 417 | 17.375 | 732.0003 | 403869.4732
| 418 | 4.6071 | 731.0678 | 4.5503 | 4.6 | 418 | 17.4167 | 731.0678 | 404600.541
| 419 | 4.5503 | 730.1365 | 4.4935 | 4.5 | 419 | 17.4583 | 730.1365 | 405330.6775
| 420 | 4.4935 | 729.2064 | 4.4369 | 4.4 | 420 | 17.5 | 729.2064 | 406059.8839
| 421 | 4.4369 | 728.2774 | 4.3802 | 4.4 | 421 | 17.5417 | 728.2774 | 406788.1612
| 422 | 4.3802 | 727.3496 | 4.3237 | 4.3 | 422 | 17.5833 | 727.3496 | 407515.5109
| 423 | 4.3237 | 726.423 | 4.2672 | 4.3 | 423 | 17.625 | 726.423 | 408241.9339
| 424 | 4.2672 | 725.4976 | 4.2108 | 4.2 | 424 | 17.6667 | 725.4976 | 408967.4315
| 425 | 4.2108 | 724.5734 | 4.1545 | 4.2 | 425 | 17.7083 | 724.5734 | 409692.0049
| 426 | 4.1545 | 723.6503 | 4.0983 | 4.1 | 426 | 17.75 | 723.6503 | 410415.6553
| 427 | 4.0983 | 722.7285 | 4.0421 | 4 | 427 | 17.7917 | 722.7285 | 411138.3838
| 428 | 4.0421 | 721.8078 | 3.986 | 4 | 428 | 17.8333 | 721.8078 | 411860.1915
| 429 | 3.986 | 720.8882 | 3.93 | 3.9 | 429 | 17.875 | 720.8882 | 412581.0798
| 430 | 3.93 | 719.9699 | 3.874 | 3.9 | 430 | 17.9167 | 719.9699 | 413301.0497
| 431 | 3.874 | 719.0527 | 3.8181 | 3.8 | 431 | 17.9583 | 719.0527 | 414020.1024
| 432 | 3.8181 | 718.1367 | 3.7623 | 3.8 | 432 | 18 | 718.1367 | 414738.239
| 433 | 3.7623 | 717.2218 | 3.7065 | 3.7 | 433 | 18.0417 | 717.2218 | 415455.4609
| 434 | 3.7065 | 716.3081 | 3.6509 | 3.7 | 434 | 18.0833 | 716.3081 | 416171.769
| 435 | 3.6509 | 715.3956 | 3.5952 | 3.6 | 435 | 18.125 | 715.3956 | 416887.1646
| 436 | 3.5952 | 714.4843 | 3.5397 | 3.5 | 436 | 18.1667 | 714.4843 | 417601.6489
| 437 | 3.5397 | 713.5741 | 3.4842 | 3.5 | 437 | 18.2083 | 713.5741 | 418315.2229
| 438 | 3.4842 | 712.665 | 3.4288 | 3.4 | 438 | 18.25 | 712.665 | 419027.8879
| 439 | 3.4288 | 711.7571 | 3.3735 | 3.4 | 439 | 18.2917 | 711.7571 | 419739.6451
| 440 | 3.3735 | 710.8504 | 3.3183 | 3.3 | 440 | 18.3333 | 710.8504 | 420450.4955
| 441 | 3.3183 | 709.9448 | 3.2631 | 3.3 | 441 | 18.375 | 709.9448 | 421160.4403
| 442 | 3.2631 | 709.0404 | 3.208 | 3.2 | 442 | 18.4167 | 709.0404 | 421869.4808
| 443 | 3.208 | 708.1372 | 3.1529 | 3.2 | 443 | 18.4583 | 708.1372 | 422577.6179
| 444 | 3.1529 | 707.235 | 3.098 | 3.1 | 444 | 18.5 | 707.235 | 423284.853
| 445 | 3.098 | 706.3341 | 3.043 | 3 | 445 | 18.5417 | 706.3341 | 423991.1871
| 446 | 3.043 | 705.4343 | 2.9882 | 3 | 446 | 18.5833 | 705.4343 | 424696.6213
| 447 | 2.9882 | 704.5356 | 2.9335 | 2.9 | 447 | 18.625 | 704.5356 | 425401.1569
| 448 | 2.9335 | 703.6381 | 2.8788 | 2.9 | 448 | 18.6667 | 703.6381 | 426104.795
| 449 | 2.8788 | 702.7417 | 2.8241 | 2.8 | 449 | 18.7083 | 702.7417 | 426807.5367
| 450 | 2.8241 | 701.8464 | 2.7696 | 2.8 | 450 | 18.75 | 701.8464 | 427509.3831
| 451 | 2.7696 | 700.9524 | 2.7151 | 2.7 | 451 | 18.7917 | 700.9524 | 428210.3355
| 452 | 2.7151 | 700.0594 | 2.6607 | 2.7 | 452 | 18.8333 | 700.0594 | 428910.3949
| 453 | 2.6607 | 699.1676 | 2.6063 | 2.6 | 453 | 18.875 | 699.1676 | 429609.5624
| 454 | 2.6063 | 698.2769 | 2.5521 | 2.6 | 454 | 18.9167 | 698.2769 | 430307.8393
| 455 | 2.5521 | 697.3873 | 2.4978 | 2.5 | 455 | 18.9583 | 697.3873 | 431005.2266
| 456 | 2.4978 | 696.4989 | 2.4437 | 2.4 | 456 | 19 | 696.4989 | 431701.7256
| 457 | 2.4437 | 695.6116 | 2.3896 | 2.4 | 457 | 19.0417 | 695.6116 | 432397.3372
| 458 | 2.3896 | 694.7255 | 2.3356 | 2.3 | 458 | 19.0833 | 694.7255 | 433092.0626
| 459 | 2.3356 | 693.8404 | 2.2817 | 2.3 | 459 | 19.125 | 693.8404 | 433785.9031
| 460 | 2.2817 | 692.9565 | 2.2278 | 2.2 | 460 | 19.1667 | 692.9565 | 434478.8596
| 461 | 2.2278 | 692.0738 | 2.174 | 2.2 | 461 | 19.2083 | 692.0738 | 435170.9334
| 462 | 2.174 | 691.1921 | 2.1203 | 2.1 | 462 | 19.25 | 691.1921 | 435862.1255
| 463 | 2.1203 | 690.3116 | 2.0667 | 2.1 | 463 | 19.2917 | 690.3116 | 436552.4371
| 464 | 2.0667 | 689.4322 | 2.0131 | 2 | 464 | 19.3333 | 689.4322 | 437241.8693
| 465 | 2.0131 | 688.5539 | 1.9595 | 2 | 465 | 19.375 | 688.5539 | 437930.4232
| 466 | 1.9595 | 687.6767 | 1.9061 | 1.9 | 466 | 19.4167 | 687.6767 | 438618.0999
| 467 | 1.9061 | 686.8007 | 1.8527 | 1.9 | 467 | 19.4583 | 686.8007 | 439304.9006
| 468 | 1.8527 | 685.9257 | 1.7994 | 1.8 | 468 | 19.5 | 685.9257 | 439990.8263
| 469 | 1.7994 | 685.0519 | 1.7461 | 1.7 | 469 | 19.5417 | 685.0519 | 440675.8782
| 470 | 1.7461 | 684.1792 | 1.693 | 1.7 | 470 | 19.5833 | 684.1792 | 441360.0575
| 471 | 1.693 | 683.3076 | 1.6398 | 1.6 | 471 | 19.625 | 683.3076 | 442043.3651
| 472 | 1.6398 | 682.4372 | 1.5868 | 1.6 | 472 | 19.6667 | 682.4372 | 442725.8023
| 473 | 1.5868 | 681.5678 | 1.5338 | 1.5 | 473 | 19.7083 | 681.5678 | 443407.37
| 474 | 1.5338 | 680.6995 | 1.4809 | 1.5 | 474 | 19.75 | 680.6995 | 444088.0696
| 475 | 1.4809 | 679.8324 | 1.4281 | 1.4 | 475 | 19.7917 | 679.8324 | 444767.9019
| 476 | 1.4281 | 678.9663 | 1.3753 | 1.4 | 476 | 19.8333 | 678.9663 | 445446.8682
| 477 | 1.3753 | 678.1013 | 1.3226 | 1.3 | 477 | 19.875 | 678.1013 | 446124.9696
| 478 | 1.3226 | 677.2375 | 1.2699 | 1.3 | 478 | 19.9167 | 677.2375 | 446802.207
| 479 | 1.2699 | 676.3747 | 1.2174 | 1.2 | 479 | 19.9583 | 676.3747 | 447478.5818
| 480 | 1.2174 | 675.5131 | 1.1649 | 1.2 | 480 | 20 | 675.5131 | 448154.0949
| 481 | 1.1649 | 674.6525 | 1.1124 | 1.1 | 481 | 20.0417 | 674.6525 | 448828.7474
| 482 | 1.1124 | 673.7931 | 1.06 | 1.1 | 482 | 20.0833 | 673.7931 | 449502.5405
| 483 | 1.06 | 672.9347 | 1.0077 | 1 | 483 | 20.125 | 672.9347 | 450175.4752
| 484 | 1.0077 | 672.0775 | 0.9555 | 1 | 484 | 20.1667 | 672.0775 | 450847.5527
| 485 | 0.9555 | 671.2213 | 0.90332 | 0.9 | 485 | 20.2083 | 671.2213 | 451518.774
| 486 | 0.90332 | 670.3662 | 0.85121 | 0.9 | 486 | 20.25 | 670.3662 | 452189.1402
| 487 | 0.85121 | 669.5122 | 0.79917 | 0.8 | 487 | 20.2917 | 669.5122 | 452858.6524
| 488 | 0.79917 | 668.6593 | 0.7472 | 0.7 | 488 | 20.3333 | 668.6593 | 453527.3117
| 489 | 0.7472 | 667.8075 | 0.69529 | 0.7 | 489 | 20.375 | 667.8075 | 454195.1191
| 490 | 0.69529 | 666.9567 | 0.64345 | 0.6 | 490 | 20.4167 | 666.9567 | 454862.0759
| 491 | 0.64345 | 666.1071 | 0.59167 | 0.6 | 491 | 20.4583 | 666.1071 | 455528.183
| 492 | 0.59167 | 665.2585 | 0.53996 | 0.5 | 492 | 20.5 | 665.2585 | 456193.4415
| 493 | 0.53996 | 664.411 | 0.48831 | 0.5 | 493 | 20.5417 | 664.411 | 456857.8525
| 494 | 0.48831 | 663.5646 | 0.43673 | 0.4 | 494 | 20.5833 | 663.5646 | 457521.4171
| 495 | 0.43673 | 662.7193 | 0.38522 | 0.4 | 495 | 20.625 | 662.7193 | 458184.1364
| 496 | 0.38522 | 661.875 | 0.33377 | 0.3 | 496 | 20.6667 | 661.875 | 458846.0114
| 497 | 0.33377 | 661.0318 | 0.28239 | 0.3 | 497 | 20.7083 | 661.0318 | 459507.0432
| 498 | 0.28239 | 660.1897 | 0.23107 | 0.2 | 498 | 20.75 | 660.1897 | 460167.233
| 499 | 0.23107 | 659.3487 | 0.17982 | 0.2 | 499 | 20.7917 | 659.3487 | 460826.5817
| 500 | 0.17982 | 658.5087 | 0.12864 | 0.1 | 500 | 20.8333 | 658.5087 | 461485.0905
| 501 | 0.12864 | 657.6699 | 0.077516 | 0.1 | 501 | 20.875 | 657.6699 | 462142.7603
| 502 | 0.077516 | 656.832 | 0.02646 | 0 | 502 | 20.9167 | 656.832 | 462799.5923
| 503 | 0.02646 | 655.9953 | -0.024531 | 0 | 503 | 20.9583 | 655.9953 | 463455.5876
| 504 | -0.024531 | 655.1596 | -0.075456 | -0.1 | 504 | 21 | 655.1596 | 464110.7472
| 505 | -0.075456 | 654.325 | -0.12632 | -0.1 | 505 | 21.0417 | 654.325 | 464765.0722
| 506 | -0.12632 | 653.4914 | -0.17711 | -0.2 | 506 | 21.0833 | 653.4914 | 465418.5636
| 507 | -0.17711 | 652.6589 | -0.22784 | -0.2 | 507 | 21.125 | 652.6589 | 466071.2225
| 508 | -0.22784 | 651.8275 | -0.27851 | -0.3 | 508 | 21.1667 | 651.8275 | 466723.05
| 509 | -0.27851 | 650.9971 | -0.32911 | -0.3 | 509 | 21.2083 | 650.9971 | 467374.0471
| 510 | -0.32911 | 650.1678 | -0.37965 | -0.4 | 510 | 21.25 | 650.1678 | 468024.2149
| 511 | -0.37965 | 649.3395 | -0.43012 | -0.4 | 511 | 21.2917 | 649.3395 | 468673.5544
| 512 | -0.43012 | 648.5123 | -0.48053 | -0.5 | 512 | 21.3333 | 648.5123 | 469322.0667
| 513 | -0.48053 | 647.6861 | -0.53088 | -0.5 | 513 | 21.375 | 647.6861 | 469969.7528
| 514 | -0.53088 | 646.861 | -0.58116 | -0.6 | 514 | 21.4167 | 646.861 | 470616.6138
| 515 | -0.58116 | 646.037 | -0.63138 | -0.6 | 515 | 21.4583 | 646.037 | 471262.6508
| 516 | -0.63138 | 645.214 | -0.68153 | -0.7 | 516 | 21.5 | 645.214 | 471907.8648
| 517 | -0.68153 | 644.392 | -0.73162 | -0.7 | 517 | 21.5417 | 644.392 | 472552.2568
| 518 | -0.73162 | 643.5711 | -0.78164 | -0.8 | 518 | 21.5833 | 643.5711 | 473195.828
| 519 | -0.78164 | 642.7513 | -0.8316 | -0.8 | 519 | 21.625 | 642.7513 | 473838.5792
| 520 | -0.8316 | 641.9324 | -0.8815 | -0.9 | 520 | 21.6667 | 641.9324 | 474480.5117
| 521 | -0.8815 | 641.1147 | -0.93134 | -0.9 | 521 | 21.7083 | 641.1147 | 475121.6263
| 522 | -0.93134 | 640.2979 | -0.98111 | -1 | 522 | 21.75 | 640.2979 | 475761.9243
| 523 | -0.98111 | 639.4822 | -1.0308 | -1 | 523 | 21.7917 | 639.4822 | 476401.4065
| 524 | -1.0308 | 638.6676 | -1.0805 | -1.1 | 524 | 21.8333 | 638.6676 | 477040.0741
| 525 | -1.0805 | 637.854 | -1.13 | -1.1 | 525 | 21.875 | 637.854 | 477677.9281
| 526 | -1.13 | 637.0414 | -1.1796 | -1.2 | 526 | 21.9167 | 637.0414 | 478314.9695
| 527 | -1.1796 | 636.2299 | -1.229 | -1.2 | 527 | 21.9583 | 636.2299 | 478951.1994
| 528 | -1.229 | 635.4194 | -1.2784 | -1.3 | 528 | 22 | 635.4194 | 479586.6187
| 529 | -1.2784 | 634.6099 | -1.3277 | -1.3 | 529 | 22.0417 | 634.6099 | 480221.2286
| 530 | -1.3277 | 633.8014 | -1.377 | -1.4 | 530 | 22.0833 | 633.8014 | 480855.03
| 531 | -1.377 | 632.994 | -1.4262 | -1.4 | 531 | 22.125 | 632.994 | 481488.024
| 532 | -1.4262 | 632.1876 | -1.4753 | -1.5 | 532 | 22.1667 | 632.1876 | 482120.2117
| 533 | -1.4753 | 631.3823 | -1.5244 | -1.5 | 533 | 22.2083 | 631.3823 | 482751.5939
| 534 | -1.5244 | 630.5779 | -1.5734 | -1.6 | 534 | 22.25 | 630.5779 | 483382.1719
| 535 | -1.5734 | 629.7746 | -1.6224 | -1.6 | 535 | 22.2917 | 629.7746 | 484011.9465
| 536 | -1.6224 | 628.9723 | -1.6713 | -1.7 | 536 | 22.3333 | 628.9723 | 484640.9189
| 537 | -1.6713 | 628.1711 | -1.7201 | -1.7 | 537 | 22.375 | 628.1711 | 485269.0899
| 538 | -1.7201 | 627.3708 | -1.7689 | -1.8 | 538 | 22.4167 | 627.3708 | 485896.4608
| 539 | -1.7689 | 626.5716 | -1.8176 | -1.8 | 539 | 22.4583 | 626.5716 | 486523.0324
| 540 | -1.8176 | 625.7734 | -1.8662 | -1.9 | 540 | 22.5 | 625.7734 | 487148.8058
| 541 | -1.8662 | 624.9762 | -1.9148 | -1.9 | 541 | 22.5417 | 624.9762 | 487773.782
| 542 | -1.9148 | 624.18 | -1.9633 | -2 | 542 | 22.5833 | 624.18 | 488397.9621
| 543 | -1.9633 | 623.3849 | -2.0118 | -2 | 543 | 22.625 | 623.3849 | 489021.3469
| 544 | -2.0118 | 622.5907 | -2.0602 | -2.1 | 544 | 22.6667 | 622.5907 | 489643.9377
| 545 | -2.0602 | 621.7976 | -2.1085 | -2.1 | 545 | 22.7083 | 621.7976 | 490265.7353
| 546 | -2.1085 | 621.0055 | -2.1568 | -2.2 | 546 | 22.75 | 621.0055 | 490886.7408
| 547 | -2.1568 | 620.2144 | -2.205 | -2.2 | 547 | 22.7917 | 620.2144 | 491506.9551
| 548 | -2.205 | 619.4243 | -2.2531 | -2.3 | 548 | 22.8333 | 619.4243 | 492126.3794
| 549 | -2.2531 | 618.6352 | -2.3012 | -2.3 | 549 | 22.875 | 618.6352 | 492745.0146
| 550 | -2.3012 | 617.8471 | -2.3492 | -2.3 | 550 | 22.9167 | 617.8471 | 493362.8617
| 551 | -2.3492 | 617.06 | -2.3972 | -2.4 | 551 | 22.9583 | 617.06 | 493979.9216
| 552 | -2.3972 | 616.2739 | -2.4451 | -2.4 | 552 | 23 | 616.2739 | 494596.1955
| 553 | -2.4451 | 615.4888 | -2.4929 | -2.5 | 553 | 23.0417 | 615.4888 | 495211.6843
| 554 | -2.4929 | 614.7047 | -2.5407 | -2.5 | 554 | 23.0833 | 614.7047 | 495826.389
| 555 | -2.5407 | 613.9216 | -2.5884 | -2.6 | 555 | 23.125 | 613.9216 | 496440.3107
| 556 | -2.5884 | 613.1395 | -2.6361 | -2.6 | 556 | 23.1667 | 613.1395 | 497053.4502
| 557 | -2.6361 | 612.3584 | -2.6837 | -2.7 | 557 | 23.2083 | 612.3584 | 497665.8087
| 558 | -2.6837 | 611.5784 | -2.7312 | -2.7 | 558 | 23.25 | 611.5784 | 498277.387
| 559 | -2.7312 | 610.7992 | -2.7787 | -2.8 | 559 | 23.2917 | 610.7992 | 498888.1863
| 560 | -2.7787 | 610.0211 | -2.8261 | -2.8 | 560 | 23.3333 | 610.0211 | 499498.2074
| 561 | -2.8261 | 609.244 | -2.8735 | -2.9 | 561 | 23.375 | 609.244 | 500107.4514
| 562 | -2.8735 | 608.4679 | -2.9208 | -2.9 | 562 | 23.4167 | 608.4679 | 500715.9193
| 563 | -2.9208 | 607.6927 | -2.968 | -3 | 563 | 23.4583 | 607.6927 | 501323.612
| 564 | -2.968 | 606.9186 | -3.0152 | -3 | 564 | 23.5 | 606.9186 | 501930.5306
| 565 | -3.0152 | 606.1454 | -3.0623 | -3.1 | 565 | 23.5417 | 606.1454 | 502536.676
| 566 | -3.0623 | 605.3732 | -3.1094 | -3.1 | 566 | 23.5833 | 605.3732 | 503142.0493
| 567 | -3.1094 | 604.602 | -3.1564 | -3.2 | 567 | 23.625 | 604.602 | 503746.6513
| 568 | -3.1564 | 603.8318 | -3.2033 | -3.2 | 568 | 23.6667 | 603.8318 | 504350.4831
| 569 | -3.2033 | 603.0626 | -3.2502 | -3.3 | 569 | 23.7083 | 603.0626 | 504953.5457
| 570 | -3.2502 | 602.2943 | -3.297 | -3.3 | 570 | 23.75 | 602.2943 | 505555.84
| 571 | -3.297 | 601.527 | -3.3438 | -3.3 | 571 | 23.7917 | 601.527 | 506157.3671
| 572 | -3.3438 | 600.7607 | -3.3904 | -3.4 | 572 | 23.8333 | 600.7607 | 506758.1278
| 573 | -3.3904 | 599.9954 | -3.4371 | -3.4 | 573 | 23.875 | 599.9954 | 507358.1232
| 574 | -3.4371 | 599.2311 | -3.4837 | -3.5 | 574 | 23.9167 | 599.2311 | 507957.3543
| 575 | -3.4837 | 598.4677 | -3.5302 | -3.5 | 575 | 23.9583 | 598.4677 | 508555.822
| 576 | -3.5302 | 597.7053 | -3.5766 | -3.6 | 576 | 24 | 597.7053 | 509153.5273
| 577 | -3.5766 | 596.9439 | -3.623 | -3.6 | 577 | 24.0417 | 596.9439 | 509750.4711
| 578 | -3.623 | 596.1834 | -3.6694 | -3.7 | 578 | 24.0833 | 596.1834 | 510346.6545
| 579 | -3.6694 | 595.4239 | -3.7157 | -3.7 | 579 | 24.125 | 595.4239 | 510942.0785
| 580 | -3.7157 | 594.6654 | -3.7619 | -3.8 | 580 | 24.1667 | 594.6654 | 511536.7438
| 581 | -3.7619 | 593.9078 | -3.8081 | -3.8 | 581 | 24.2083 | 593.9078 | 512130.6517
| 582 | -3.8081 | 593.1512 | -3.8542 | -3.9 | 582 | 24.25 | 593.1512 | 512723.8029
| 583 | -3.8542 | 592.3956 | -3.9002 | -3.9 | 583 | 24.2917 | 592.3956 | 513316.1985
| 584 | -3.9002 | 591.6409 | -3.9462 | -3.9 | 584 | 24.3333 | 591.6409 | 513907.8394
| 585 | -3.9462 | 590.8872 | -3.9921 | -4 | 585 | 24.375 | 590.8872 | 514498.7266
| 586 | -3.9921 | 590.1345 | -4.038 | -4 | 586 | 24.4167 | 590.1345 | 515088.8611
| 587 | -4.038 | 589.3827 | -4.0838 | -4.1 | 587 | 24.4583 | 589.3827 | 515678.2438
| 588 | -4.0838 | 588.6319 | -4.1296 | -4.1 | 588 | 24.5 | 588.6319 | 516266.8757
| 589 | -4.1296 | 587.882 | -4.1753 | -4.2 | 589 | 24.5417 | 587.882 | 516854.7577
| 590 | -4.1753 | 587.1331 | -4.2209 | -4.2 | 590 | 24.5833 | 587.1331 | 517441.8908
| 591 | -4.2209 | 586.3851 | -4.2665 | -4.3 | 591 | 24.625 | 586.3851 | 518028.2759
| 592 | -4.2665 | 585.6381 | -4.312 | -4.3 | 592 | 24.6667 | 585.6381 | 518613.914
| 593 | -4.312 | 584.892 | -4.3575 | -4.4 | 593 | 24.7083 | 584.892 | 519198.806
| 594 | -4.3575 | 584.1469 | -4.4029 | -4.4 | 594 | 24.75 | 584.1469 | 519782.9529
| 595 | -4.4029 | 583.4028 | -4.4482 | -4.4 | 595 | 24.7917 | 583.4028 | 520366.3557
| 596 | -4.4482 | 582.6596 | -4.4935 | -4.5 | 596 | 24.8333 | 582.6596 | 520949.0153
| 597 | -4.4935 | 581.9173 | -4.5387 | -4.5 | 597 | 24.875 | 581.9173 | 521530.9326
| 598 | -4.5387 | 581.176 | -4.5839 | -4.6 | 598 | 24.9167 | 581.176 | 522112.1086
| 599 | -4.5839 | 580.4356 | -4.629 | -4.6 | 599 | 24.9583 | 580.4356 | 522692.5442
| 600 | -4.629 | 579.6962 | -4.6741 | -4.7 | 600 | 25 | 579.6962 | 523272.2403
| 601 | -4.6741 | 578.9577 | -4.7191 | -4.7 | 601 | 25.0417 | 578.9577 | 523851.198
| 602 | -4.7191 | 578.2201 | -4.764 | -4.8 | 602 | 25.0833 | 578.2201 | 524429.4182
| 603 | -4.764 | 577.4835 | -4.8089 | -4.8 | 603 | 25.125 | 577.4835 | 525006.9017
| 604 | -4.8089 | 576.7479 | -4.8538 | -4.9 | 604 | 25.1667 | 576.7479 | 525583.6495
| 605 | -4.8538 | 576.0131 | -4.8985 | -4.9 | 605 | 25.2083 | 576.0131 | 526159.6627
| 606 | -4.8985 | 575.2793 | -4.9433 | -4.9 | 606 | 25.25 | 575.2793 | 526734.942
| 607 | -4.9433 | 574.5465 | -4.9879 | -5 | 607 | 25.2917 | 574.5465 | 527309.4885
| 608 | -4.9879 | 573.8145 | -5.0325 | -5 | 608 | 25.3333 | 573.8145 | 527883.303
| 609 | -5.0325 | 573.0835 | -5.0771 | -5.1 | 609 | 25.375 | 573.0835 | 528456.3865
| 610 | -5.0771 | 572.3535 | -5.1215 | -5.1 | 610 | 25.4167 | 572.3535 | 529028.74
| 611 | -5.1215 | 571.6243 | -5.166 | -5.2 | 611 | 25.4583 | 571.6243 | 529600.3644
| 612 | -5.166 | 570.8961 | -5.2104 | -5.2 | 612 | 25.5 | 570.8961 | 530171.2605
| 613 | -5.2104 | 570.1689 | -5.2547 | -5.3 | 613 | 25.5417 | 570.1689 | 530741.4293
| 614 | -5.2547 | 569.4425 | -5.2989 | -5.3 | 614 | 25.5833 | 569.4425 | 531310.8718
| 615 | -5.2989 | 568.7171 | -5.3431 | -5.3 | 615 | 25.625 | 568.7171 | 531879.5889
| 616 | -5.3431 | 567.9926 | -5.3873 | -5.4 | 616 | 25.6667 | 567.9926 | 532447.5815
| 617 | -5.3873 | 567.269 | -5.4314 | -5.4 | 617 | 25.7083 | 567.269 | 533014.8505
| 618 | -5.4314 | 566.5463 | -5.4754 | -5.5 | 618 | 25.75 | 566.5463 | 533581.3968
| 619 | -5.4754 | 565.8246 | -5.5194 | -5.5 | 619 | 25.7917 | 565.8246 | 534147.2214
| 620 | -5.5194 | 565.1038 | -5.5633 | -5.6 | 620 | 25.8333 | 565.1038 | 534712.3252
| 621 | -5.5633 | 564.3839 | -5.6072 | -5.6 | 621 | 25.875 | 564.3839 | 535276.7091
| 622 | -5.6072 | 563.6649 | -5.651 | -5.7 | 622 | 25.9167 | 563.6649 | 535840.374
| 623 | -5.651 | 562.9468 | -5.6948 | -5.7 | 623 | 25.9583 | 562.9468 | 536403.3208
| 624 | -5.6948 | 562.2297 | -5.7385 | -5.7 | 624 | 26 | 562.2297 | 536965.5505
| 625 | -5.7385 | 561.5134 | -5.7821 | -5.8 | 625 | 26.0417 | 561.5134 | 537527.0639
| 626 | -5.7821 | 560.7981 | -5.8257 | -5.8 | 626 | 26.0833 | 560.7981 | 538087.862
| 627 | -5.8257 | 560.0837 | -5.8693 | -5.9 | 627 | 26.125 | 560.0837 | 538647.9457
| 628 | -5.8693 | 559.3702 | -5.9127 | -5.9 | 628 | 26.1667 | 559.3702 | 539207.3159
| 629 | -5.9127 | 558.6576 | -5.9562 | -6 | 629 | 26.2083 | 558.6576 | 539765.9735
| 630 | -5.9562 | 557.9459 | -5.9995 | -6 | 630 | 26.25 | 557.9459 | 540323.9194
| 631 | -5.9995 | 557.2351 | -6.0428 | -6 | 631 | 26.2917 | 557.2351 | 540881.1546
| 632 | -6.0428 | 556.5253 | -6.0861 | -6.1 | 632 | 26.3333 | 556.5253 | 541437.6798
| 633 | -6.0861 | 555.8163 | -6.1293 | -6.1 | 633 | 26.375 | 555.8163 | 541993.4961
| 634 | -6.1293 | 555.1082 | -6.1725 | -6.2 | 634 | 26.4167 | 555.1082 | 542548.6043
| 635 | -6.1725 | 554.401 | -6.2155 | -6.2 | 635 | 26.4583 | 554.401 | 543103.0054
| 636 | -6.2155 | 553.6948 | -6.2586 | -6.3 | 636 | 26.5 | 553.6948 | 543656.7002
| 637 | -6.2586 | 552.9894 | -6.3016 | -6.3 | 637 | 26.5417 | 552.9894 | 544209.6896
| 638 | -6.3016 | 552.285 | -6.3445 | -6.3 | 638 | 26.5833 | 552.285 | 544761.9745
| 639 | -6.3445 | 551.5814 | -6.3874 | -6.4 | 639 | 26.625 | 551.5814 | 545313.5559
| 640 | -6.3874 | 550.8787 | -6.4302 | -6.4 | 640 | 26.6667 | 550.8787 | 545864.4346
| 641 | -6.4302 | 550.1769 | -6.473 | -6.5 | 641 | 26.7083 | 550.1769 | 546414.6115
| 642 | -6.473 | 549.476 | -6.5157 | -6.5 | 642 | 26.75 | 549.476 | 546964.0876
| 643 | -6.5157 | 548.7761 | -6.5583 | -6.6 | 643 | 26.7917 | 548.7761 | 547512.8637
| 644 | -6.5583 | 548.077 | -6.6009 | -6.6 | 644 | 26.8333 | 548.077 | 548060.9406
| 645 | -6.6009 | 547.3787 | -6.6435 | -6.6 | 645 | 26.875 | 547.3787 | 548608.3194
| 646 | -6.6435 | 546.6814 | -6.686 | -6.7 | 646 | 26.9167 | 546.6814 | 549155.0008
| 647 | -6.686 | 545.985 | -6.7284 | -6.7 | 647 | 26.9583 | 545.985 | 549700.9858
| 648 | -6.7284 | 545.2895 | -6.7708 | -6.8 | 648 | 27 | 545.2895 | 550246.2752
| 649 | -6.7708 | 544.5948 | -6.8131 | -6.8 | 649 | 27.0417 | 544.5948 | 550790.87
| 650 | -6.8131 | 543.901 | -6.8554 | -6.9 | 650 | 27.0833 | 543.901 | 551334.7711
| 651 | -6.8554 | 543.2081 | -6.8976 | -6.9 | 651 | 27.125 | 543.2081 | 551877.9792
| 652 | -6.8976 | 542.5161 | -6.9398 | -6.9 | 652 | 27.1667 | 542.5161 | 552420.4953
| 653 | -6.9398 | 541.825 | -6.9819 | -7 | 653 | 27.2083 | 541.825 | 552962.3203
| 654 | -6.9819 | 541.1348 | -7.024 | -7 | 654 | 27.25 | 541.1348 | 553503.4551
| 655 | -7.024 | 540.4454 | -7.066 | -7.1 | 655 | 27.2917 | 540.4454 | 554043.9005
| 656 | -7.066 | 539.7569 | -7.1079 | -7.1 | 656 | 27.3333 | 539.7569 | 554583.6574
| 657 | -7.1079 | 539.0693 | -7.1498 | -7.1 | 657 | 27.375 | 539.0693 | 555122.7267
| 658 | -7.1498 | 538.3826 | -7.1917 | -7.2 | 658 | 27.4167 | 538.3826 | 555661.1093
| 659 | -7.1917 | 537.6967 | -7.2335 | -7.2 | 659 | 27.4583 | 537.6967 | 556198.806
| 660 | -7.2335 | 537.0117 | -7.2752 | -7.3 | 660 | 27.5 | 537.0117 | 556735.8177
| 661 | -7.2752 | 536.3276 | -7.3169 | -7.3 | 661 | 27.5417 | 536.3276 | 557272.1453
| 662 | -7.3169 | 535.6444 | -7.3586 | -7.4 | 662 | 27.5833 | 535.6444 | 557807.7897
| 663 | -7.3586 | 534.962 | -7.4001 | -7.4 | 663 | 27.625 | 534.962 | 558342.7517
| 664 | -7.4001 | 534.2805 | -7.4417 | -7.4 | 664 | 27.6667 | 534.2805 | 558877.0322
| 665 | -7.4417 | 533.5999 | -7.4831 | -7.5 | 665 | 27.7083 | 533.5999 | 559410.632
| 666 | -7.4831 | 532.9201 | -7.5246 | -7.5 | 666 | 27.75 | 532.9201 | 559943.5521
| 667 | -7.5246 | 532.2412 | -7.5659 | -7.6 | 667 | 27.7917 | 532.2412 | 560475.7933
| 668 | -7.5659 | 531.5632 | -7.6073 | -7.6 | 668 | 27.8333 | 531.5632 | 561007.3565
| 669 | -7.6073 | 530.886 | -7.6485 | -7.6 | 669 | 27.875 | 530.886 | 561538.2425
| 670 | -7.6485 | 530.2097 | -7.6897 | -7.7 | 670 | 27.9167 | 530.2097 | 562068.4522
| 671 | -7.6897 | 529.5342 | -7.7309 | -7.7 | 671 | 27.9583 | 529.5342 | 562597.9864
| 672 | -7.7309 | 528.8596 | -7.772 | -7.8 | 672 | 28 | 528.8596 | 563126.846
| 673 | -7.772 | 528.1859 | -7.8131 | -7.8 | 673 | 28.0417 | 528.1859 | 563655.032
| 674 | -7.8131 | 527.5131 | -7.8541 | -7.9 | 674 | 28.0833 | 527.5131 | 564182.545
| 675 | -7.8541 | 526.841 | -7.895 | -7.9 | 675 | 28.125 | 526.841 | 564709.386
| 676 | -7.895 | 526.1699 | -7.9359 | -7.9 | 676 | 28.1667 | 526.1699 | 565235.5559
| 677 | -7.9359 | 525.4996 | -7.9768 | -8 | 677 | 28.2083 | 525.4996 | 565761.0555
| 678 | -7.9768 | 524.8301 | -8.0176 | -8 | 678 | 28.25 | 524.8301 | 566285.8856
| 679 | -8.0176 | 524.1615 | -8.0583 | -8.1 | 679 | 28.2917 | 524.1615 | 566810.0472
| 680 | -8.0583 | 523.4938 | -8.099 | -8.1 | 680 | 28.3333 | 523.4938 | 567333.541
| 681 | -8.099 | 522.8269 | -8.1396 | -8.1 | 681 | 28.375 | 522.8269 | 567856.3679
| 682 | -8.1396 | 522.1609 | -8.1802 | -8.2 | 682 | 28.4167 | 522.1609 | 568378.5288
| 683 | -8.1802 | 521.4957 | -8.2208 | -8.2 | 683 | 28.4583 | 521.4957 | 568900.0244
| 684 | -8.2208 | 520.8313 | -8.2612 | -8.3 | 684 | 28.5 | 520.8313 | 569420.8558
| 685 | -8.2612 | 520.1678 | -8.3017 | -8.3 | 685 | 28.5417 | 520.1678 | 569941.0236
| 686 | -8.3017 | 519.5052 | -8.3421 | -8.3 | 686 | 28.5833 | 519.5052 | 570460.5288
| 687 | -8.3421 | 518.8434 | -8.3824 | -8.4 | 687 | 28.625 | 518.8434 | 570979.3721
| 688 | -8.3824 | 518.1824 | -8.4227 | -8.4 | 688 | 28.6667 | 518.1824 | 571497.5545
| 689 | -8.4227 | 517.5223 | -8.4629 | -8.5 | 689 | 28.7083 | 517.5223 | 572015.0768
| 690 | -8.4629 | 516.863 | -8.5031 | -8.5 | 690 | 28.75 | 516.863 | 572531.9398
| 691 | -8.5031 | 516.2045 | -8.5432 | -8.5 | 691 | 28.7917 | 516.2045 | 573048.1443
| 692 | -8.5432 | 515.5469 | -8.5833 | -8.6 | 692 | 28.8333 | 515.5469 | 573563.6912
| 693 | -8.5833 | 514.8902 | -8.6233 | -8.6 | 693 | 28.875 | 514.8902 | 574078.5814
| 694 | -8.6233 | 514.2342 | -8.6633 | -8.7 | 694 | 28.9167 | 514.2342 | 574592.8156
| 695 | -8.6633 | 513.5791 | -8.7032 | -8.7 | 695 | 28.9583 | 513.5791 | 575106.3948
| 696 | -8.7032 | 512.9249 | -8.743 | -8.7 | 696 | 29 | 512.9249 | 575619.3197
| 697 | -8.743 | 512.2715 | -8.7829 | -8.8 | 697 | 29.0417 | 512.2715 | 576131.5911
| 698 | -8.7829 | 511.6189 | -8.8226 | -8.8 | 698 | 29.0833 | 511.6189 | 576643.21
| 699 | -8.8226 | 510.9671 | -8.8624 | -8.9 | 699 | 29.125 | 510.9671 | 577154.1771
| 700 | -8.8624 | 510.3162 | -8.902 | -8.9 | 700 | 29.1667 | 510.3162 | 577664.4932
| 701 | -8.902 | 509.6661 | -8.9416 | -8.9 | 701 | 29.2083 | 509.6661 | 578174.1593
| 702 | -8.9416 | 509.0168 | -8.9812 | -9 | 702 | 29.25 | 509.0168 | 578683.176
| 703 | -8.9812 | 508.3683 | -9.0207 | -9 | 703 | 29.2917 | 508.3683 | 579191.5444
| 704 | -9.0207 | 507.7207 | -9.0602 | -9.1 | 704 | 29.3333 | 507.7207 | 579699.2651
| 705 | -9.0602 | 507.0739 | -9.0996 | -9.1 | 705 | 29.375 | 507.0739 | 580206.339
| 706 | -9.0996 | 506.4279 | -9.139 | -9.1 | 706 | 29.4167 | 506.4279 | 580712.7669
| 707 | -9.139 | 505.7828 | -9.1783 | -9.2 | 707 | 29.4583 | 505.7828 | 581218.5497
| 708 | -9.1783 | 505.1385 | -9.2175 | -9.2 | 708 | 29.5 | 505.1385 | 581723.6882
| 709 | -9.2175 | 504.4949 | -9.2568 | -9.3 | 709 | 29.5417 | 504.4949 | 582228.1831
| 710 | -9.2568 | 503.8523 | -9.2959 | -9.3 | 710 | 29.5833 | 503.8523 | 582732.0354
| 711 | -9.2959 | 503.2104 | -9.335 | -9.3 | 711 | 29.625 | 503.2104 | 583235.2457
| 712 | -9.335 | 502.5693 | -9.3741 | -9.4 | 712 | 29.6667 | 502.5693 | 583737.8151
| 713 | -9.3741 | 501.9291 | -9.4131 | -9.4 | 713 | 29.7083 | 501.9291 | 584239.7442
| 714 | -9.4131 | 501.2897 | -9.4521 | -9.5 | 714 | 29.75 | 501.2897 | 584741.0339
| 715 | -9.4521 | 500.6511 | -9.491 | -9.5 | 715 | 29.7917 | 500.6511 | 585241.6849
| 716 | -9.491 | 500.0133 | -9.5299 | -9.5 | 716 | 29.8333 | 500.0133 | 585741.6982
| 717 | -9.5299 | 499.3763 | -9.5687 | -9.6 | 717 | 29.875 | 499.3763 | 586241.0745
| 718 | -9.5687 | 498.7401 | -9.6074 | -9.6 | 718 | 29.9167 | 498.7401 | 586739.8146
| 719 | -9.6074 | 498.1048 | -9.6462 | -9.6 | 719 | 29.9583 | 498.1048 | 587237.9194
| 720 | -9.6462 | 497.4702 | -9.6848 | -9.7 | 720 | 30 | 497.4702 | 587735.3897
| 721 | -9.6848 | 496.8365 | -9.7235 | -9.7 | 721 | 30.0417 | 496.8365 | 588232.2261
| 722 | -9.7235 | 496.2036 | -9.762 | -9.8 | 722 | 30.0833 | 496.2036 | 588728.4297
| 723 | -9.762 | 495.5714 | -9.8005 | -9.8 | 723 | 30.125 | 495.5714 | 589224.0011
| 724 | -9.8005 | 494.9401 | -9.839 | -9.8 | 724 | 30.1667 | 494.9401 | 589718.9412
| 725 | -9.839 | 494.3096 | -9.8774 | -9.9 | 725 | 30.2083 | 494.3096 | 590213.2508
| 726 | -9.8774 | 493.6799 | -9.9158 | -9.9 | 726 | 30.25 | 493.6799 | 590706.9307
| 727 | -9.9158 | 493.051 | -9.9541 | -10 | 727 | 30.2917 | 493.051 | 591199.9817
| 728 | -9.9541 | 492.4229 | -9.9924 | -10 | 728 | 30.3333 | 492.4229 | 591692.4045
| 729 | -9.9924 | 491.7956 | -10.0306 | -10 | 729 | 30.375 | 491.7956 | 592184.2001
| 730 | -10.0306 | 491.169 | -10.0688 | -10.1 | 730 | 30.4167 | 491.169 | 592675.3691
| 731 | -10.0688 | 490.5433 | -10.107 | -10.1 | 731 | 30.4583 | 490.5433 | 593165.9125
| 732 | -10.107 | 489.9184 | -10.145 | -10.1 | 732 | 30.5 | 489.9184 | 593655.8309
| 733 | -10.145 | 489.2943 | -10.1831 | -10.2 | 733 | 30.5417 | 489.2943 | 594145.1252
| 734 | -10.1831 | 488.671 | -10.221 | -10.2 | 734 | 30.5833 | 488.671 | 594633.7961
| 735 | -10.221 | 488.0484 | -10.259 | -10.3 | 735 | 30.625 | 488.0484 | 595121.8446
| 736 | -10.259 | 487.4267 | -10.2969 | -10.3 | 736 | 30.6667 | 487.4267 | 595609.2713
| 737 | -10.2969 | 486.8058 | -10.3347 | -10.3 | 737 | 30.7083 | 486.8058 | 596096.077
| 738 | -10.3347 | 486.1856 | -10.3725 | -10.4 | 738 | 30.75 | 486.1856 | 596582.2626
| 739 | -10.3725 | 485.5662 | -10.4102 | -10.4 | 739 | 30.7917 | 485.5662 | 597067.8289
| 740 | -10.4102 | 484.9477 | -10.4479 | -10.4 | 740 | 30.8333 | 484.9477 | 597552.7766
| 741 | -10.4479 | 484.3299 | -10.4856 | -10.5 | 741 | 30.875 | 484.3299 | 598037.1064
| 742 | -10.4856 | 483.7129 | -10.5232 | -10.5 | 742 | 30.9167 | 483.7129 | 598520.8193
| 743 | -10.5232 | 483.0967 | -10.5607 | -10.6 | 743 | 30.9583 | 483.0967 | 599003.916
| 744 | -10.5607 | 482.4812 | -10.5982 | -10.6 | 744 | 31 | 482.4812 | 599486.3972
| 745 | -10.5982 | 481.8666 | -10.6357 | -10.6 | 745 | 31.0417 | 481.8666 | 599968.2638
| 746 | -10.6357 | 481.2527 | -10.6731 | -10.7 | 746 | 31.0833 | 481.2527 | 600449.5165
| 747 | -10.6731 | 480.6397 | -10.7105 | -10.7 | 747 | 31.125 | 480.6397 | 600930.1562
| 748 | -10.7105 | 480.0274 | -10.7478 | -10.7 | 748 | 31.1667 | 480.0274 | 601410.1835
| 749 | -10.7478 | 479.4158 | -10.785 | -10.8 | 749 | 31.2083 | 479.4158 | 601889.5994
| 750 | -10.785 | 478.8051 | -10.8223 | -10.8 | 750 | 31.25 | 478.8051 | 602368.4045
| 751 | -10.8223 | 478.1951 | -10.8594 | -10.9 | 751 | 31.2917 | 478.1951 | 602846.5996
| 752 | -10.8594 | 477.5859 | -10.8966 | -10.9 | 752 | 31.3333 | 477.5859 | 603324.1855
| 753 | -10.8966 | 476.9775 | -10.9336 | -10.9 | 753 | 31.375 | 476.9775 | 603801.1631
| 754 | -10.9336 | 476.3699 | -10.9707 | -11 | 754 | 31.4167 | 476.3699 | 604277.533
| 755 | -10.9707 | 475.763 | -11.0076 | -11 | 755 | 31.4583 | 475.763 | 604753.296
| 756 | -11.0076 | 475.157 | -11.0446 | -11 | 756 | 31.5 | 475.157 | 605228.453
| 757 | -11.0446 | 474.5516 | -11.0815 | -11.1 | 757 | 31.5417 | 474.5516 | 605703.0046
| 758 | -11.0815 | 473.9471 | -11.1183 | -11.1 | 758 | 31.5833 | 473.9471 | 606176.9517
| 759 | -11.1183 | 473.3433 | -11.1551 | -11.2 | 759 | 31.625 | 473.3433 | 606650.2951
| 760 | -11.1551 | 472.7403 | -11.1918 | -11.2 | 760 | 31.6667 | 472.7403 | 607123.0354
| 761 | -11.1918 | 472.1381 | -11.2285 | -11.2 | 761 | 31.7083 | 472.1381 | 607595.1735
| 762 | -11.2285 | 471.5366 | -11.2652 | -11.3 | 762 | 31.75 | 471.5366 | 608066.7101
| 763 | -11.2652 | 470.9359 | -11.3018 | -11.3 | 763 | 31.7917 | 470.9359 | 608537.646
| 764 | -11.3018 | 470.336 | -11.3384 | -11.3 | 764 | 31.8333 | 470.336 | 609007.982
| 765 | -11.3384 | 469.7368 | -11.3749 | -11.4 | 765 | 31.875 | 469.7368 | 609477.7188
| 766 | -11.3749 | 469.1384 | -11.4113 | -11.4 | 766 | 31.9167 | 469.1384 | 609946.8572
| 767 | -11.4113 | 468.5408 | -11.4478 | -11.4 | 767 | 31.9583 | 468.5408 | 610415.398
| 768 | -11.4478 | 467.9439 | -11.4841 | -11.5 | 768 | 32 | 467.9439 | 610883.3418
| 769 | -11.4841 | 467.3477 | -11.5205 | -11.5 | 769 | 32.0417 | 467.3477 | 611350.6896
| 770 | -11.5205 | 466.7524 | -11.5567 | -11.6 | 770 | 32.0833 | 466.7524 | 611817.442
| 771 | -11.5567 | 466.1578 | -11.593 | -11.6 | 771 | 32.125 | 466.1578 | 612283.5997
| 772 | -11.593 | 465.5639 | -11.6292 | -11.6 | 772 | 32.1667 | 465.5639 | 612749.1636
| 773 | -11.6292 | 464.9708 | -11.6653 | -11.7 | 773 | 32.2083 | 464.9708 | 613214.1345
| 774 | -11.6653 | 464.3785 | -11.7014 | -11.7 | 774 | 32.25 | 464.3785 | 613678.513
| 775 | -11.7014 | 463.7869 | -11.7375 | -11.7 | 775 | 32.2917 | 463.7869 | 614142.2999
| 776 | -11.7375 | 463.1961 | -11.7735 | -11.8 | 776 | 32.3333 | 463.1961 | 614605.4959
| 777 | -11.7735 | 462.606 | -11.8094 | -11.8 | 777 | 32.375 | 462.606 | 615068.1019
| 778 | -11.8094 | 462.0167 | -11.8453 | -11.8 | 778 | 32.4167 | 462.0167 | 615530.1186
| 779 | -11.8453 | 461.4281 | -11.8812 | -11.9 | 779 | 32.4583 | 461.4281 | 615991.5467
| 780 | -11.8812 | 460.8403 | -11.917 | -11.9 | 780 | 32.5 | 460.8403 | 616452.387
| 781 | -11.917 | 460.2532 | -11.9528 | -12 | 781 | 32.5417 | 460.2532 | 616912.6402
| 782 | -11.9528 | 459.6669 | -11.9885 | -12 | 782 | 32.5833 | 459.6669 | 617372.3071
| 783 | -11.9885 | 459.0813 | -12.0242 | -12 | 783 | 32.625 | 459.0813 | 617831.3884
| 784 | -12.0242 | 458.4965 | -12.0598 | -12.1 | 784 | 32.6667 | 458.4965 | 618289.8848
| 785 | -12.0598 | 457.9124 | -12.0954 | -12.1 | 785 | 32.7083 | 457.9124 | 618747.7972
| 786 | -12.0954 | 457.329 | -12.131 | -12.1 | 786 | 32.75 | 457.329 | 619205.1262
| 787 | -12.131 | 456.7464 | -12.1665 | -12.2 | 787 | 32.7917 | 456.7464 | 619661.8726
| 788 | -12.1665 | 456.1646 | -12.2019 | -12.2 | 788 | 32.8333 | 456.1646 | 620118.0372
| 789 | -12.2019 | 455.5834 | -12.2374 | -12.2 | 789 | 32.875 | 455.5834 | 620573.6206
| 790 | -12.2374 | 455.0031 | -12.2727 | -12.3 | 790 | 32.9167 | 455.0031 | 621028.6237
| 791 | -12.2727 | 454.4234 | -12.308 | -12.3 | 791 | 32.9583 | 454.4234 | 621483.0471
| 792 | -12.308 | 453.8445 | -12.3433 | -12.3 | 792 | 33 | 453.8445 | 621936.8916
| 793 | -12.3433 | 453.2664 | -12.3786 | -12.4 | 793 | 33.0417 | 453.2664 | 622390.1579
| 794 | -12.3786 | 452.6889 | -12.4137 | -12.4 | 794 | 33.0833 | 452.6889 | 622842.8469
| 795 | -12.4137 | 452.1122 | -12.4489 | -12.4 | 795 | 33.125 | 452.1122 | 623294.9591
| 796 | -12.4489 | 451.5363 | -12.484 | -12.5 | 796 | 33.1667 | 451.5363 | 623746.4954
| 797 | -12.484 | 450.9611 | -12.519 | -12.5 | 797 | 33.2083 | 450.9611 | 624197.4564
| 798 | -12.519 | 450.3866 | -12.554 | -12.6 | 798 | 33.25 | 450.3866 | 624647.843
| 799 | -12.554 | 449.8128 | -12.589 | -12.6 | 799 | 33.2917 | 449.8128 | 625097.6558
| 800 | -12.589 | 449.2398 | -12.6239 | -12.6 | 800 | 33.3333 | 449.2398 | 625546.8956
| 801 | -12.6239 | 448.6675 | -12.6588 | -12.7 | 801 | 33.375 | 448.6675 | 625995.5631
| 802 | -12.6588 | 448.0959 | -12.6936 | -12.7 | 802 | 33.4167 | 448.0959 | 626443.659
| 803 | -12.6936 | 447.5251 | -12.7284 | -12.7 | 803 | 33.4583 | 447.5251 | 626891.184
| 804 | -12.7284 | 446.955 | -12.7632 | -12.8 | 804 | 33.5 | 446.955 | 627338.139
| 805 | -12.7632 | 446.3856 | -12.7979 | -12.8 | 805 | 33.5417 | 446.3856 | 627784.5246
| 806 | -12.7979 | 445.8169 | -12.8325 | -12.8 | 806 | 33.5833 | 445.8169 | 628230.3415
| 807 | -12.8325 | 445.249 | -12.8671 | -12.9 | 807 | 33.625 | 445.249 | 628675.5905
| 808 | -12.8671 | 444.6818 | -12.9017 | -12.9 | 808 | 33.6667 | 444.6818 | 629120.2722
| 809 | -12.9017 | 444.1153 | -12.9362 | -12.9 | 809 | 33.7083 | 444.1153 | 629564.3875
| 810 | -12.9362 | 443.5495 | -12.9707 | -13 | 810 | 33.75 | 443.5495 | 630007.937
| 811 | -12.9707 | 442.9844 | -13.0051 | -13 | 811 | 33.7917 | 442.9844 | 630450.9214
| 812 | -13.0051 | 442.4201 | -13.0395 | -13 | 812 | 33.8333 | 442.4201 | 630893.3416
| 813 | -13.0395 | 441.8565 | -13.0739 | -13.1 | 813 | 33.875 | 441.8565 | 631335.1981
| 814 | -13.0739 | 441.2936 | -13.1082 | -13.1 | 814 | 33.9167 | 441.2936 | 631776.4917
| 815 | -13.1082 | 440.7314 | -13.1424 | -13.1 | 815 | 33.9583 | 440.7314 | 632217.2231
| 816 | -13.1424 | 440.17 | -13.1766 | -13.2 | 816 | 34 | 440.17 | 632657.3931
| 817 | -13.1766 | 439.6092 | -13.2108 | -13.2 | 817 | 34.0417 | 439.6092 | 633097.0024
| 818 | -13.2108 | 439.0492 | -13.2449 | -13.2 | 818 | 34.0833 | 439.0492 | 633536.0516
| 819 | -13.2449 | 438.4899 | -13.279 | -13.3 | 819 | 34.125 | 438.4899 | 633974.5415
| 820 | -13.279 | 437.9313 | -13.3131 | -13.3 | 820 | 34.1667 | 437.9313 | 634412.4728
| 821 | -13.3131 | 437.3734 | -13.3471 | -13.3 | 821 | 34.2083 | 437.3734 | 634849.8462
| 822 | -13.3471 | 436.8162 | -13.381 | -13.4 | 822 | 34.25 | 436.8162 | 635286.6624
| 823 | -13.381 | 436.2598 | -13.4149 | -13.4 | 823 | 34.2917 | 436.2598 | 635722.9221
| 824 | -13.4149 | 435.704 | -13.4488 | -13.4 | 824 | 34.3333 | 435.704 | 636158.6261
| 825 | -13.4488 | 435.1489 | -13.4826 | -13.5 | 825 | 34.375 | 435.1489 | 636593.7751
| 826 | -13.4826 | 434.5946 | -13.5164 | -13.5 | 826 | 34.4167 | 434.5946 | 637028.3696
| 827 | -13.5164 | 434.0409 | -13.5501 | -13.6 | 827 | 34.4583 | 434.0409 | 637462.4106
| 828 | -13.5501 | 433.488 | -13.5838 | -13.6 | 828 | 34.5 | 433.488 | 637895.8986
| 829 | -13.5838 | 432.9358 | -13.6175 | -13.6 | 829 | 34.5417 | 432.9358 | 638328.8344
| 830 | -13.6175 | 432.3843 | -13.6511 | -13.7 | 830 | 34.5833 | 432.3843 | 638761.2186
| 831 | -13.6511 | 431.8334 | -13.6847 | -13.7 | 831 | 34.625 | 431.8334 | 639193.0521
| 832 | -13.6847 | 431.2833 | -13.7182 | -13.7 | 832 | 34.6667 | 431.2833 | 639624.3354
| 833 | -13.7182 | 430.7339 | -13.7517 | -13.8 | 833 | 34.7083 | 430.7339 | 640055.0693
| 834 | -13.7517 | 430.1852 | -13.7851 | -13.8 | 834 | 34.75 | 430.1852 | 640485.2544
| 835 | -13.7851 | 429.6371 | -13.8185 | -13.8 | 835 | 34.7917 | 429.6371 | 640914.8916
| 836 | -13.8185 | 429.0898 | -13.8518 | -13.9 | 836 | 34.8333 | 429.0898 | 641343.9814
| 837 | -13.8518 | 428.5432 | -13.8852 | -13.9 | 837 | 34.875 | 428.5432 | 641772.5245
| 838 | -13.8852 | 427.9973 | -13.9184 | -13.9 | 838 | 34.9167 | 427.9973 | 642200.5218
| 839 | -13.9184 | 427.452 | -13.9516 | -14 | 839 | 34.9583 | 427.452 | 642627.9738
| 840 | -13.9516 | 426.9075 | -13.9848 | -14 | 840 | 35 | 426.9075 | 643054.8813
| 841 | -13.9848 | 426.3636 | -14.018 | -14 | 841 | 35.0417 | 426.3636 | 643481.2449
| 842 | -14.018 | 425.8205 | -14.0511 | -14.1 | 842 | 35.0833 | 425.8205 | 643907.0654
| 843 | -14.0511 | 425.278 | -14.0841 | -14.1 | 843 | 35.125 | 425.278 | 644332.3434
| 844 | -14.0841 | 424.7362 | -14.1171 | -14.1 | 844 | 35.1667 | 424.7362 | 644757.0796
| 845 | -14.1171 | 424.1952 | -14.1501 | -14.2 | 845 | 35.2083 | 424.1952 | 645181.2748
| 846 | -14.1501 | 423.6548 | -14.183 | -14.2 | 846 | 35.25 | 423.6548 | 645604.9295
| 847 | -14.183 | 423.1151 | -14.2159 | -14.2 | 847 | 35.2917 | 423.1151 | 646028.0446
| 848 | -14.2159 | 422.576 | -14.2488 | -14.2 | 848 | 35.3333 | 422.576 | 646450.6206
| 849 | -14.2488 | 422.0377 | -14.2816 | -14.3 | 849 | 35.375 | 422.0377 | 646872.6583
| 850 | -14.2816 | 421.5001 | -14.3144 | -14.3 | 850 | 35.4167 | 421.5001 | 647294.1584
| 851 | -14.3144 | 420.9631 | -14.3471 | -14.3 | 851 | 35.4583 | 420.9631 | 647715.1215
| 852 | -14.3471 | 420.4268 | -14.3798 | -14.4 | 852 | 35.5 | 420.4268 | 648135.5483
| 853 | -14.3798 | 419.8912 | -14.4124 | -14.4 | 853 | 35.5417 | 419.8912 | 648555.4396
| 854 | -14.4124 | 419.3563 | -14.445 | -14.4 | 854 | 35.5833 | 419.3563 | 648974.7959
| 855 | -14.445 | 418.8221 | -14.4775 | -14.5 | 855 | 35.625 | 418.8221 | 649393.618
| 856 | -14.4775 | 418.2886 | -14.5101 | -14.5 | 856 | 35.6667 | 418.2886 | 649811.9066
| 857 | -14.5101 | 417.7557 | -14.5425 | -14.5 | 857 | 35.7083 | 417.7557 | 650229.6622
| 858 | -14.5425 | 417.2235 | -14.575 | -14.6 | 858 | 35.75 | 417.2235 | 650646.8857
| 859 | -14.575 | 416.692 | -14.6074 | -14.6 | 859 | 35.7917 | 416.692 | 651063.5777
| 860 | -14.6074 | 416.1611 | -14.6397 | -14.6 | 860 | 35.8333 | 416.1611 | 651479.7389
| 861 | -14.6397 | 415.631 | -14.672 | -14.7 | 861 | 35.875 | 415.631 | 651895.3699
| 862 | -14.672 | 415.1015 | -14.7043 | -14.7 | 862 | 35.9167 | 415.1015 | 652310.4714
| 863 | -14.7043 | 414.5727 | -14.7365 | -14.7 | 863 | 35.9583 | 414.5727 | 652725.0441
| 864 | -14.7365 | 414.0446 | -14.7687 | -14.8 | 864 | 36 | 414.0446 | 653139.0886
| 865 | -14.7687 | 413.5171 | -14.8008 | -14.8 | 865 | 36.0417 | 413.5171 | 653552.6057
| 866 | -14.8008 | 412.9903 | -14.8329 | -14.8 | 866 | 36.0833 | 412.9903 | 653965.5961
| 867 | -14.8329 | 412.4642 | -14.865 | -14.9 | 867 | 36.125 | 412.4642 | 654378.0603
| 868 | -14.865 | 411.9387 | -14.897 | -14.9 | 868 | 36.1667 | 411.9387 | 654789.999
| 869 | -14.897 | 411.414 | -14.929 | -14.9 | 869 | 36.2083 | 411.414 | 655201.413
| 870 | -14.929 | 410.8899 | -14.9609 | -15 | 870 | 36.25 | 410.8899 | 655612.3028
| 871 | -14.9609 | 410.3664 | -14.9928 | -15 | 871 | 36.2917 | 410.3664 | 656022.6693
| 872 | -14.9928 | 409.8436 | -15.0247 | -15 | 872 | 36.3333 | 409.8436 | 656432.5129
| 873 | -15.0247 | 409.3215 | -15.0565 | -15.1 | 873 | 36.375 | 409.3215 | 656841.8344
| 874 | -15.0565 | 408.8001 | -15.0883 | -15.1 | 874 | 36.4167 | 408.8001 | 657250.6345
| 875 | -15.0883 | 408.2793 | -15.12 | -15.1 | 875 | 36.4583 | 408.2793 | 657658.9138
| 876 | -15.12 | 407.7592 | -15.1517 | -15.2 | 876 | 36.5 | 407.7592 | 658066.673
| 877 | -15.1517 | 407.2397 | -15.1834 | -15.2 | 877 | 36.5417 | 407.2397 | 658473.9127
| 878 | -15.1834 | 406.7209 | -15.215 | -15.2 | 878 | 36.5833 | 406.7209 | 658880.6337
| 879 | -15.215 | 406.2028 | -15.2465 | -15.2 | 879 | 36.625 | 406.2028 | 659286.8365
| 880 | -15.2465 | 405.6853 | -15.2781 | -15.3 | 880 | 36.6667 | 405.6853 | 659692.5218
| 881 | -15.2781 | 405.1685 | -15.3096 | -15.3 | 881 | 36.7083 | 405.1685 | 660097.6904
| 882 | -15.3096 | 404.6524 | -15.341 | -15.3 | 882 | 36.75 | 404.6524 | 660502.3427
| 883 | -15.341 | 404.1369 | -15.3724 | -15.4 | 883 | 36.7917 | 404.1369 | 660906.4796
| 884 | -15.3724 | 403.622 | -15.4038 | -15.4 | 884 | 36.8333 | 403.622 | 661310.1016
| 885 | -15.4038 | 403.1079 | -15.4352 | -15.4 | 885 | 36.875 | 403.1079 | 661713.2095
| 886 | -15.4352 | 402.5943 | -15.4664 | -15.5 | 886 | 36.9167 | 402.5943 | 662115.8038
| 887 | -15.4664 | 402.0814 | -15.4977 | -15.5 | 887 | 36.9583 | 402.0814 | 662517.8852
| 888 | -15.4977 | 401.5692 | -15.5289 | -15.5 | 888 | 37 | 401.5692 | 662919.4545
| 889 | -15.5289 | 401.0577 | -15.5601 | -15.6 | 889 | 37.0417 | 401.0577 | 663320.5121
| 890 | -15.5601 | 400.5467 | -15.5912 | -15.6 | 890 | 37.0833 | 400.5467 | 663721.0589
| 891 | -15.5912 | 400.0365 | -15.6223 | -15.6 | 891 | 37.125 | 400.0365 | 664121.0953
| 892 | -15.6223 | 399.5269 | -15.6534 | -15.7 | 892 | 37.1667 | 399.5269 | 664520.6222
| 893 | -15.6534 | 399.0179 | -15.6844 | -15.7 | 893 | 37.2083 | 399.0179 | 664919.6401
| 894 | -15.6844 | 398.5096 | -15.7154 | -15.7 | 894 | 37.25 | 398.5096 | 665318.1497
| 895 | -15.7154 | 398.0019 | -15.7463 | -15.7 | 895 | 37.2917 | 398.0019 | 665716.1516
| 896 | -15.7463 | 397.4949 | -15.7772 | -15.8 | 896 | 37.3333 | 397.4949 | 666113.6464
| 897 | -15.7772 | 396.9885 | -15.8081 | -15.8 | 897 | 37.375 | 396.9885 | 666510.6349
| 898 | -15.8081 | 396.4828 | -15.8389 | -15.8 | 898 | 37.4167 | 396.4828 | 666907.1177
| 899 | -15.8389 | 395.9777 | -15.8697 | -15.9 | 899 | 37.4583 | 395.9777 | 667303.0954
| 900 | -15.8697 | 395.4732 | -15.9004 | -15.9 | 900 | 37.5 | 395.4732 | 667698.5686
| 901 | -15.9004 | 394.9694 | -15.9311 | -15.9 | 901 | 37.5417 | 394.9694 | 668093.538
| 902 | -15.9311 | 394.4663 | -15.9618 | -16 | 902 | 37.5833 | 394.4663 | 668488.0043
| 903 | -15.9618 | 393.9637 | -15.9924 | -16 | 903 | 37.625 | 393.9637 | 668881.968
| 904 | -15.9924 | 393.4619 | -16.023 | -16 | 904 | 37.6667 | 393.4619 | 669275.4299
| 905 | -16.023 | 392.9606 | -16.0535 | -16.1 | 905 | 37.7083 | 392.9606 | 669668.3905
| 906 | -16.0535 | 392.46 | -16.084 | -16.1 | 906 | 37.75 | 392.46 | 670060.8505
| 907 | -16.084 | 391.9601 | -16.1145 | -16.1 | 907 | 37.7917 | 391.9601 | 670452.8106
| 908 | -16.1145 | 391.4607 | -16.1449 | -16.1 | 908 | 37.8333 | 391.4607 | 670844.2713
| 909 | -16.1449 | 390.962 | -16.1753 | -16.2 | 909 | 37.875 | 390.962 | 671235.2333
| 910 | -16.1753 | 390.464 | -16.2057 | -16.2 | 910 | 37.9167 | 390.464 | 671625.6973
| 911 | -16.2057 | 389.9666 | -16.236 | -16.2 | 911 | 37.9583 | 389.9666 | 672015.6639
| 912 | -16.236 | 389.4698 | -16.2662 | -16.3 | 912 | 38 | 389.4698 | 672405.1337
| 913 | -16.2662 | 388.9736 | -16.2965 | -16.3 | 913 | 38.0417 | 388.9736 | 672794.1073
| 914 | -16.2965 | 388.4781 | -16.3267 | -16.3 | 914 | 38.0833 | 388.4781 | 673182.5854
| 915 | -16.3267 | 387.9832 | -16.3568 | -16.4 | 915 | 38.125 | 387.9832 | 673570.5686
| 916 | -16.3568 | 387.4889 | -16.3869 | -16.4 | 916 | 38.1667 | 387.4889 | 673958.0575
| 917 | -16.3869 | 386.9953 | -16.417 | -16.4 | 917 | 38.2083 | 386.9953 | 674345.0528
| 918 | -16.417 | 386.5023 | -16.4471 | -16.4 | 918 | 38.25 | 386.5023 | 674731.5551
| 919 | -16.4471 | 386.0099 | -16.4771 | -16.5 | 919 | 38.2917 | 386.0099 | 675117.565
| 920 | -16.4771 | 385.5182 | -16.507 | -16.5 | 920 | 38.3333 | 385.5182 | 675503.0832
| 921 | -16.507 | 385.0271 | -16.537 | -16.5 | 921 | 38.375 | 385.0271 | 675888.1103
| 922 | -16.537 | 384.5366 | -16.5669 | -16.6 | 922 | 38.4167 | 384.5366 | 676272.6468
| 923 | -16.5669 | 384.0467 | -16.5967 | -16.6 | 923 | 38.4583 | 384.0467 | 676656.6935
| 924 | -16.5967 | 383.5574 | -16.6265 | -16.6 | 924 | 38.5 | 383.5574 | 677040.251
| 925 | -16.6265 | 383.0688 | -16.6563 | -16.7 | 925 | 38.5417 | 383.0688 | 677423.3198
| 926 | -16.6563 | 382.5808 | -16.686 | -16.7 | 926 | 38.5833 | 382.5808 | 677805.9006
| 927 | -16.686 | 382.0934 | -16.7157 | -16.7 | 927 | 38.625 | 382.0934 | 678187.9941
| 928 | -16.7157 | 381.6067 | -16.7454 | -16.7 | 928 | 38.6667 | 381.6067 | 678569.6008
| 929 | -16.7454 | 381.1205 | -16.775 | -16.8 | 929 | 38.7083 | 381.1205 | 678950.7213
| 930 | -16.775 | 380.635 | -16.8046 | -16.8 | 930 | 38.75 | 380.635 | 679331.3563
| 931 | -16.8046 | 380.1501 | -16.8342 | -16.8 | 931 | 38.7917 | 380.1501 | 679711.5065
| 932 | -16.8342 | 379.6658 | -16.8637 | -16.9 | 932 | 38.8333 | 379.6658 | 680091.1723
| 933 | -16.8637 | 379.1822 | -16.8931 | -16.9 | 933 | 38.875 | 379.1822 | 680470.3545
| 934 | -16.8931 | 378.6991 | -16.9226 | -16.9 | 934 | 38.9167 | 378.6991 | 680849.0536
| 935 | -16.9226 | 378.2167 | -16.952 | -17 | 935 | 38.9583 | 378.2167 | 681227.2703
| 936 | -16.952 | 377.7349 | -16.9813 | -17 | 936 | 39 | 377.7349 | 681605.0052
| 937 | -16.9813 | 377.2537 | -17.0107 | -17 | 937 | 39.0417 | 377.2537 | 681982.2589
| 938 | -17.0107 | 376.7731 | -17.04 | -17 | 938 | 39.0833 | 376.7731 | 682359.032
| 939 | -17.04 | 376.2931 | -17.0692 | -17.1 | 939 | 39.125 | 376.2931 | 682735.3251
| 940 | -17.0692 | 375.8137 | -17.0984 | -17.1 | 940 | 39.1667 | 375.8137 | 683111.1388
| 941 | -17.0984 | 375.335 | -17.1276 | -17.1 | 941 | 39.2083 | 375.335 | 683486.4738
| 942 | -17.1276 | 374.8568 | -17.1567 | -17.2 | 942 | 39.25 | 374.8568 | 683861.3306
| 943 | -17.1567 | 374.3793 | -17.1858 | -17.2 | 943 | 39.2917 | 374.3793 | 684235.7099
| 944 | -17.1858 | 373.9024 | -17.2149 | -17.2 | 944 | 39.3333 | 373.9024 | 684609.6122
| 945 | -17.2149 | 373.426 | -17.2439 | -17.2 | 945 | 39.375 | 373.426 | 684983.0383
| 946 | -17.2439 | 372.9503 | -17.2729 | -17.3 | 946 | 39.4167 | 372.9503 | 685355.9886
| 947 | -17.2729 | 372.4752 | -17.3019 | -17.3 | 947 | 39.4583 | 372.4752 | 685728.4638
| 948 | -17.3019 | 372.0007 | -17.3308 | -17.3 | 948 | 39.5 | 372.0007 | 686100.4645
| 949 | -17.3308 | 371.5268 | -17.3597 | -17.4 | 949 | 39.5417 | 371.5268 | 686471.9913
| 950 | -17.3597 | 371.0535 | -17.3885 | -17.4 | 950 | 39.5833 | 371.0535 | 686843.0448
| 951 | -17.3885 | 370.5808 | -17.4173 | -17.4 | 951 | 39.625 | 370.5808 | 687213.6256
| 952 | -17.4173 | 370.1087 | -17.4461 | -17.4 | 952 | 39.6667 | 370.1087 | 687583.7343
| 953 | -17.4461 | 369.6372 | -17.4748 | -17.5 | 953 | 39.7083 | 369.6372 | 687953.3715
| 954 | -17.4748 | 369.1663 | -17.5035 | -17.5 | 954 | 39.75 | 369.1663 | 688322.5378
| 955 | -17.5035 | 368.696 | -17.5322 | -17.5 | 955 | 39.7917 | 368.696 | 688691.2339
| 956 | -17.5322 | 368.2264 | -17.5608 | -17.6 | 956 | 39.8333 | 368.2264 | 689059.4602
| 957 | -17.5608 | 367.7573 | -17.5894 | -17.6 | 957 | 39.875 | 367.7573 | 689427.2175
| 958 | -17.5894 | 367.2888 | -17.6179 | -17.6 | 958 | 39.9167 | 367.2888 | 689794.5062
| 959 | -17.6179 | 366.8209 | -17.6464 | -17.6 | 959 | 39.9583 | 366.8209 | 690161.3271
| 960 | -17.6464 | 366.3536 | -17.6749 | -17.7 | 960 | 40 | 366.3536 | 690527.6807
| 961 | -17.6749 | 365.8869 | -17.7033 | -17.7 | 961 | 40.0417 | 365.8869 | 690893.5675
| 962 | -17.7033 | 365.4207 | -17.7318 | -17.7 | 962 | 40.0833 | 365.4207 | 691258.9883
| 963 | -17.7318 | 364.9552 | -17.7601 | -17.8 | 963 | 40.125 | 364.9552 | 691623.9435
| 964 | -17.7601 | 364.4903 | -17.7885 | -17.8 | 964 | 40.1667 | 364.4903 | 691988.4338
| 965 | -17.7885 | 364.026 | -17.8167 | -17.8 | 965 | 40.2083 | 364.026 | 692352.4598
| 966 | -17.8167 | 363.5622 | -17.845 | -17.8 | 966 | 40.25 | 363.5622 | 692716.022
| 967 | -17.845 | 363.0991 | -17.8732 | -17.9 | 967 | 40.2917 | 363.0991 | 693079.1211
| 968 | -17.8732 | 362.6365 | -17.9014 | -17.9 | 968 | 40.3333 | 362.6365 | 693441.7576
| 969 | -17.9014 | 362.1745 | -17.9296 | -17.9 | 969 | 40.375 | 362.1745 | 693803.9321
| 970 | -17.9296 | 361.7132 | -17.9577 | -18 | 970 | 40.4167 | 361.7132 | 694165.6453
| 971 | -17.9577 | 361.2524 | -17.9858 | -18 | 971 | 40.4583 | 361.2524 | 694526.8976
| 972 | -17.9858 | 360.7922 | -18.0138 | -18 | 972 | 40.5 | 360.7922 | 694887.6898
| 973 | -18.0138 | 360.3325 | -18.0418 | -18 | 973 | 40.5417 | 360.3325 | 695248.0223
| 974 | -18.0418 | 359.8735 | -18.0698 | -18.1 | 974 | 40.5833 | 359.8735 | 695607.8958
| 975 | -18.0698 | 359.415 | -18.0977 | -18.1 | 975 | 40.625 | 359.415 | 695967.3109
| 976 | -18.0977 | 358.9572 | -18.1256 | -18.1 | 976 | 40.6667 | 358.9572 | 696326.268
| 977 | -18.1256 | 358.4999 | -18.1535 | -18.2 | 977 | 40.7083 | 358.4999 | 696684.7679
| 978 | -18.1535 | 358.0432 | -18.1813 | -18.2 | 978 | 40.75 | 358.0432 | 697042.8111
| 979 | -18.1813 | 357.5871 | -18.2091 | -18.2 | 979 | 40.7917 | 357.5871 | 697400.3982
| 980 | -18.2091 | 357.1315 | -18.2369 | -18.2 | 980 | 40.8333 | 357.1315 | 697757.5297
| 981 | -18.2369 | 356.6766 | -18.2646 | -18.3 | 981 | 40.875 | 356.6766 | 698114.2063
| 982 | -18.2646 | 356.2222 | -18.2923 | -18.3 | 982 | 40.9167 | 356.2222 | 698470.4285
| 983 | -18.2923 | 355.7684 | -18.32 | -18.3 | 983 | 40.9583 | 355.7684 | 698826.1969
| 984 | -18.32 | 355.3152 | -18.3476 | -18.3 | 984 | 41 | 355.3152 | 699181.512
| 985 | -18.3476 | 354.8625 | -18.3752 | -18.4 | 985 | 41.0417 | 354.8625 | 699536.3746
| 986 | -18.3752 | 354.4105 | -18.4027 | -18.4 | 986 | 41.0833 | 354.4105 | 699890.785
| 987 | -18.4027 | 353.959 | -18.4302 | -18.4 | 987 | 41.125 | 353.959 | 700244.744
| 988 | -18.4302 | 353.508 | -18.4577 | -18.5 | 988 | 41.1667 | 353.508 | 700598.252
| 989 | -18.4577 | 353.0577 | -18.4851 | -18.5 | 989 | 41.2083 | 353.0577 | 700951.3098
| 990 | -18.4851 | 352.6079 | -18.5125 | -18.5 | 990 | 41.25 | 352.6079 | 701303.9177
| 991 | -18.5125 | 352.1587 | -18.5399 | -18.5 | 991 | 41.2917 | 352.1587 | 701656.0764
| 992 | -18.5399 | 351.7101 | -18.5673 | -18.6 | 992 | 41.3333 | 351.7101 | 702007.7866
| 993 | -18.5673 | 351.2621 | -18.5946 | -18.6 | 993 | 41.375 | 351.2621 | 702359.0486
| 994 | -18.5946 | 350.8146 | -18.6218 | -18.6 | 994 | 41.4167 | 350.8146 | 702709.8632
| 995 | -18.6218 | 350.3677 | -18.6491 | -18.6 | 995 | 41.4583 | 350.3677 | 703060.2309
| 996 | -18.6491 | 349.9213 | -18.6763 | -18.7 | 996 | 41.5 | 349.9213 | 703410.1522
| 997 | -18.6763 | 349.4756 | -18.7034 | -18.7 | 997 | 41.5417 | 349.4756 | 703759.6278
| 998 | -18.7034 | 349.0304 | -18.7306 | -18.7 | 998 | 41.5833 | 349.0304 | 704108.6581
| 999 | -18.7306 | 348.5857 | -18.7577 | -18.8 | 999 | 41.625 | 348.5857 | 704457.2438
| 1000 | -18.7577 | 348.1416 | -18.7847 | -18.8 | 1000 | 41.6667 | 348.1416 | 704805.3855
| 1001 | -18.7847 | 347.6981 | -18.8117 | -18.8 | 1001 | 41.7083 | 347.6981 | 705153.0836
| 1002 | -18.8117 | 347.2552 | -18.8387 | -18.8 | 1002 | 41.75 | 347.2552 | 705500.3388
| 1003 | -18.8387 | 346.8128 | -18.8657 | -18.9 | 1003 | 41.7917 | 346.8128 | 705847.1516
| 1004 | -18.8657 | 346.371 | -18.8926 | -18.9 | 1004 | 41.8333 | 346.371 | 706193.5226
| 1005 | -18.8926 | 345.9298 | -18.9195 | -18.9 | 1005 | 41.875 | 345.9298 | 706539.4524
| 1006 | -18.9195 | 345.4891 | -18.9464 | -18.9 | 1006 | 41.9167 | 345.4891 | 706884.9414
| 1007 | -18.9464 | 345.0489 | -18.9732 | -19 | 1007 | 41.9583 | 345.0489 | 707229.9904
| 1008 | -18.9732 | 344.6094 | -19 | -19 | 1008 | 42 | 344.6094 | 707574.5998
| 1009 | -19 | 344.1704 | -19.0267 | -19 | 1009 | 42.0417 | 344.1704 | 707918.7701
| 1010 | -19.0267 | 343.7319 | -19.0534 | -19.1 | 1010 | 42.0833 | 343.7319 | 708262.502
| 1011 | -19.0534 | 343.294 | -19.0801 | -19.1 | 1011 | 42.125 | 343.294 | 708605.7961
| 1012 | -19.0801 | 342.8567 | -19.1068 | -19.1 | 1012 | 42.1667 | 342.8567 | 708948.6528
| 1013 | -19.1068 | 342.4199 | -19.1334 | -19.1 | 1013 | 42.2083 | 342.4199 | 709291.0727
| 1014 | -19.1334 | 341.9837 | -19.16 | -19.2 | 1014 | 42.25 | 341.9837 | 709633.0564
| 1015 | -19.16 | 341.548 | -19.1865 | -19.2 | 1015 | 42.2917 | 341.548 | 709974.6044
| 1016 | -19.1865 | 341.1129 | -19.213 | -19.2 | 1016 | 42.3333 | 341.1129 | 710315.7174
| 1017 | -19.213 | 340.6784 | -19.2395 | -19.2 | 1017 | 42.375 | 340.6784 | 710656.3958
| 1018 | -19.2395 | 340.2444 | -19.266 | -19.3 | 1018 | 42.4167 | 340.2444 | 710996.6402
| 1019 | -19.266 | 339.8109 | -19.2924 | -19.3 | 1019 | 42.4583 | 339.8109 | 711336.4511
| 1020 | -19.2924 | 339.378 | -19.3188 | -19.3 | 1020 | 42.5 | 339.378 | 711675.8292
| 1021 | -19.3188 | 338.9457 | -19.3451 | -19.3 | 1021 | 42.5417 | 338.9457 | 712014.7749
| 1022 | -19.3451 | 338.5139 | -19.3714 | -19.4 | 1022 | 42.5833 | 338.5139 | 712353.2888
| 1023 | -19.3714 | 338.0827 | -19.3977 | -19.4 | 1023 | 42.625 | 338.0827 | 712691.3715
| 1024 | -19.3977 | 337.652 | -19.4239 | -19.4 | 1024 | 42.6667 | 337.652 | 713029.0234
| 1025 | -19.4239 | 337.2218 | -19.4502 | -19.5 | 1025 | 42.7083 | 337.2218 | 713366.2453
| 1026 | -19.4502 | 336.7922 | -19.4763 | -19.5 | 1026 | 42.75 | 336.7922 | 713703.0375
| 1027 | -19.4763 | 336.3632 | -19.5025 | -19.5 | 1027 | 42.7917 | 336.3632 | 714039.4007
| 1028 | -19.5025 | 335.9347 | -19.5286 | -19.5 | 1028 | 42.8333 | 335.9347 | 714375.3354
| 1029 | -19.5286 | 335.5067 | -19.5547 | -19.6 | 1029 | 42.875 | 335.5067 | 714710.8422
| 1030 | -19.5547 | 335.0793 | -19.5807 | -19.6 | 1030 | 42.9167 | 335.0793 | 715045.9215
| 1031 | -19.5807 | 334.6525 | -19.6067 | -19.6 | 1031 | 42.9583 | 334.6525 | 715380.5739
| 1032 | -19.6067 | 334.2261 | -19.6327 | -19.6 | 1032 | 43 | 334.2261 | 715714.8001
| 1033 | -19.6327 | 333.8004 | -19.6587 | -19.7 | 1033 | 43.0417 | 333.8004 | 716048.6005
| 1034 | -19.6587 | 333.3751 | -19.6846 | -19.7 | 1034 | 43.0833 | 333.3751 | 716381.9756
| 1035 | -19.6846 | 332.9504 | -19.7104 | -19.7 | 1035 | 43.125 | 332.9504 | 716714.926
| 1036 | -19.7104 | 332.5263 | -19.7363 | -19.7 | 1036 | 43.1667 | 332.5263 | 717047.4523
| 1037 | -19.7363 | 332.1027 | -19.7621 | -19.8 | 1037 | 43.2083 | 332.1027 | 717379.555
| 1038 | -19.7621 | 331.6796 | -19.7879 | -19.8 | 1038 | 43.25 | 331.6796 | 717711.2345
| 1039 | -19.7879 | 331.2571 | -19.8136 | -19.8 | 1039 | 43.2917 | 331.2571 | 718042.4916
| 1040 | -19.8136 | 330.8351 | -19.8394 | -19.8 | 1040 | 43.3333 | 330.8351 | 718373.3267
| 1041 | -19.8394 | 330.4136 | -19.865 | -19.9 | 1041 | 43.375 | 330.4136 | 718703.7403
| 1042 | -19.865 | 329.9927 | -19.8907 | -19.9 | 1042 | 43.4167 | 329.9927 | 719033.7329
| 1043 | -19.8907 | 329.5723 | -19.9163 | -19.9 | 1043 | 43.4583 | 329.5723 | 719363.3052
| 1044 | -19.9163 | 329.1524 | -19.9419 | -19.9 | 1044 | 43.5 | 329.1524 | 719692.4577
| 1045 | -19.9419 | 328.7331 | -19.9674 | -20 | 1045 | 43.5417 | 328.7331 | 720021.1908
| 1046 | -19.9674 | 328.3143 | -19.993 | -20 | 1046 | 43.5833 | 328.3143 | 720349.5052
| 1047 | -19.993 | 327.8961 | -20.0185 | -20 | 1047 | 43.625 | 327.8961 | 720677.4012
| 1048 | -20.0185 | 327.4784 | -20.0439 | -20 | 1048 | 43.6667 | 327.4784 | 721004.8796
| 1049 | -20.0439 | 327.0612 | -20.0693 | -20.1 | 1049 | 43.7083 | 327.0612 | 721331.9408
| 1050 | -20.0693 | 326.6445 | -20.0947 | -20.1 | 1050 | 43.75 | 326.6445 | 721658.5854
| 1051 | -20.0947 | 326.2284 | -20.1201 | -20.1 | 1051 | 43.7917 | 326.2284 | 721984.8138
| 1052 | -20.1201 | 325.8128 | -20.1454 | -20.1 | 1052 | 43.8333 | 325.8128 | 722310.6266
| 1053 | -20.1454 | 325.3978 | -20.1707 | -20.2 | 1053 | 43.875 | 325.3978 | 722636.0244
| 1054 | -20.1707 | 324.9832 | -20.196 | -20.2 | 1054 | 43.9167 | 324.9832 | 722961.0077
| 1055 | -20.196 | 324.5692 | -20.2212 | -20.2 | 1055 | 43.9583 | 324.5692 | 723285.5769
| 1056 | -20.2212 | 324.1558 | -20.2464 | -20.2 | 1056 | 44 | 324.1558 | 723609.7327
| 1057 | -20.2464 | 323.7428 | -20.2715 | -20.3 | 1057 | 44.0417 | 323.7428 | 723933.4755
| 1058 | -20.2715 | 323.3304 | -20.2967 | -20.3 | 1058 | 44.0833 | 323.3304 | 724256.8059
| 1059 | -20.2967 | 322.9185 | -20.3218 | -20.3 | 1059 | 44.125 | 322.9185 | 724579.7244
| 1060 | -20.3218 | 322.5071 | -20.3469 | -20.3 | 1060 | 44.1667 | 322.5071 | 724902.2315
| 1061 | -20.3469 | 322.0963 | -20.3719 | -20.4 | 1061 | 44.2083 | 322.0963 | 725224.3278
| 1062 | -20.3719 | 321.6859 | -20.3969 | -20.4 | 1062 | 44.25 | 321.6859 | 725546.0137
| 1063 | -20.3969 | 321.2761 | -20.4219 | -20.4 | 1063 | 44.2917 | 321.2761 | 725867.2898
| 1064 | -20.4219 | 320.8669 | -20.4468 | -20.4 | 1064 | 44.3333 | 320.8669 | 726188.1567
| 1065 | -20.4468 | 320.4581 | -20.4717 | -20.5 | 1065 | 44.375 | 320.4581 | 726508.6148
| 1066 | -20.4717 | 320.0499 | -20.4966 | -20.5 | 1066 | 44.4167 | 320.0499 | 726828.6646
| 1067 | -20.4966 | 319.6421 | -20.5214 | -20.5 | 1067 | 44.4583 | 319.6421 | 727148.3068
| 1068 | -20.5214 | 319.2349 | -20.5463 | -20.5 | 1068 | 44.5 | 319.2349 | 727467.5417
| 1069 | -20.5463 | 318.8283 | -20.571 | -20.6 | 1069 | 44.5417 | 318.8283 | 727786.37
| 1070 | -20.571 | 318.4221 | -20.5958 | -20.6 | 1070 | 44.5833 | 318.4221 | 728104.7921
| 1071 | -20.5958 | 318.0164 | -20.6205 | -20.6 | 1071 | 44.625 | 318.0164 | 728422.8085
| 1072 | -20.6205 | 317.6113 | -20.6452 | -20.6 | 1072 | 44.6667 | 317.6113 | 728740.4198
| 1073 | -20.6452 | 317.2067 | -20.6699 | -20.7 | 1073 | 44.7083 | 317.2067 | 729057.6265
| 1074 | -20.6699 | 316.8026 | -20.6945 | -20.7 | 1074 | 44.75 | 316.8026 | 729374.4291
| 1075 | -20.6945 | 316.399 | -20.7191 | -20.7 | 1075 | 44.7917 | 316.399 | 729690.8282
| 1076 | -20.7191 | 315.996 | -20.7436 | -20.7 | 1076 | 44.8333 | 315.996 | 730006.8241
| 1077 | -20.7436 | 315.5934 | -20.7682 | -20.8 | 1077 | 44.875 | 315.5934 | 730322.4175
| 1078 | -20.7682 | 315.1914 | -20.7927 | -20.8 | 1078 | 44.9167 | 315.1914 | 730637.6089
| 1079 | -20.7927 | 314.7898 | -20.8171 | -20.8 | 1079 | 44.9583 | 314.7898 | 730952.3987
| 1080 | -20.8171 | 314.3888 | -20.8416 | -20.8 | 1080 | 45 | 314.3888 | 731266.7875
| 1081 | -20.8416 | 313.9883 | -20.866 | -20.9 | 1081 | 45.0417 | 313.9883 | 731580.7758
| 1082 | -20.866 | 313.5883 | -20.8904 | -20.9 | 1082 | 45.0833 | 313.5883 | 731894.3641
| 1083 | -20.8904 | 313.1888 | -20.9147 | -20.9 | 1083 | 45.125 | 313.1888 | 732207.553
| 1084 | -20.9147 | 312.7898 | -20.939 | -20.9 | 1084 | 45.1667 | 312.7898 | 732520.3428
| 1085 | -20.939 | 312.3914 | -20.9633 | -21 | 1085 | 45.2083 | 312.3914 | 732832.7342
| 1086 | -20.9633 | 311.9934 | -20.9875 | -21 | 1086 | 45.25 | 311.9934 | 733144.7276
| 1087 | -20.9875 | 311.5959 | -21.0118 | -21 | 1087 | 45.2917 | 311.5959 | 733456.3235
| 1088 | -21.0118 | 311.199 | -21.036 | -21 | 1088 | 45.3333 | 311.199 | 733767.5225
| 1089 | -21.036 | 310.8026 | -21.0601 | -21.1 | 1089 | 45.375 | 310.8026 | 734078.3251
| 1090 | -21.0601 | 310.4066 | -21.0842 | -21.1 | 1090 | 45.4167 | 310.4066 | 734388.7317
| 1091 | -21.0842 | 310.0112 | -21.1083 | -21.1 | 1091 | 45.4583 | 310.0112 | 734698.7429
| 1092 | -21.1083 | 309.6163 | -21.1324 | -21.1 | 1092 | 45.5 | 309.6163 | 735008.3591
| 1093 | -21.1324 | 309.2218 | -21.1564 | -21.2 | 1093 | 45.5417 | 309.2218 | 735317.5809
| 1094 | -21.1564 | 308.8279 | -21.1804 | -21.2 | 1094 | 45.5833 | 308.8279 | 735626.4088
| 1095 | -21.1804 | 308.4345 | -21.2044 | -21.2 | 1095 | 45.625 | 308.4345 | 735934.8433
| 1096 | -21.2044 | 308.0416 | -21.2284 | -21.2 | 1096 | 45.6667 | 308.0416 | 736242.8849
| 1097 | -21.2284 | 307.6491 | -21.2523 | -21.3 | 1097 | 45.7083 | 307.6491 | 736550.534
| 1098 | -21.2523 | 307.2572 | -21.2762 | -21.3 | 1098 | 45.75 | 307.2572 | 736857.7912
| 1099 | -21.2762 | 306.8658 | -21.3 | -21.3 | 1099 | 45.7917 | 306.8658 | 737164.657
| 1100 | -21.3 | 306.4749 | -21.3238 | -21.3 | 1100 | 45.8333 | 306.4749 | 737471.1318
| 1101 | -21.3238 | 306.0844 | -21.3476 | -21.3 | 1101 | 45.875 | 306.0844 | 737777.2163
| 1102 | -21.3476 | 305.6945 | -21.3714 | -21.4 | 1102 | 45.9167 | 305.6945 | 738082.9108
| 1103 | -21.3714 | 305.3051 | -21.3951 | -21.4 | 1103 | 45.9583 | 305.3051 | 738388.2159
| 1104 | -21.3951 | 304.9161 | -21.4188 | -21.4 | 1104 | 46 | 304.9161 | 738693.132
| 1105 | -21.4188 | 304.5277 | -21.4425 | -21.4 | 1105 | 46.0417 | 304.5277 | 738997.6597
| 1106 | -21.4425 | 304.1398 | -21.4661 | -21.5 | 1106 | 46.0833 | 304.1398 | 739301.7995
| 1107 | -21.4661 | 303.7523 | -21.4897 | -21.5 | 1107 | 46.125 | 303.7523 | 739605.5518
| 1108 | -21.4897 | 303.3653 | -21.5133 | -21.5 | 1108 | 46.1667 | 303.3653 | 739908.9171
| 1109 | -21.5133 | 302.9789 | -21.5369 | -21.5 | 1109 | 46.2083 | 302.9789 | 740211.896
| 1110 | -21.5369 | 302.5929 | -21.5604 | -21.6 | 1110 | 46.25 | 302.5929 | 740514.4889
| 1111 | -21.5604 | 302.2074 | -21.5839 | -21.6 | 1111 | 46.2917 | 302.2074 | 740816.6963
| 1112 | -21.5839 | 301.8224 | -21.6073 | -21.6 | 1112 | 46.3333 | 301.8224 | 741118.5188
| 1113 | -21.6073 | 301.4379 | -21.6308 | -21.6 | 1113 | 46.375 | 301.4379 | 741419.9567
| 1114 | -21.6308 | 301.0539 | -21.6542 | -21.7 | 1114 | 46.4167 | 301.0539 | 741721.0106
| 1115 | -21.6542 | 300.6704 | -21.6776 | -21.7 | 1115 | 46.4583 | 300.6704 | 742021.681
| 1116 | -21.6776 | 300.2874 | -21.7009 | -21.7 | 1116 | 46.5 | 300.2874 | 742321.9684
| 1117 | -21.7009 | 299.9048 | -21.7242 | -21.7 | 1117 | 46.5417 | 299.9048 | 742621.8733
| 1118 | -21.7242 | 299.5228 | -21.7475 | -21.7 | 1118 | 46.5833 | 299.5228 | 742921.396
| 1119 | -21.7475 | 299.1412 | -21.7707 | -21.8 | 1119 | 46.625 | 299.1412 | 743220.5372
| 1120 | -21.7707 | 298.7601 | -21.794 | -21.8 | 1120 | 46.6667 | 298.7601 | 743519.2974
| 1121 | -21.794 | 298.3795 | -21.8172 | -21.8 | 1121 | 46.7083 | 298.3795 | 743817.6769
| 1122 | -21.8172 | 297.9994 | -21.8403 | -21.8 | 1122 | 46.75 | 297.9994 | 744115.6763
| 1123 | -21.8403 | 297.6198 | -21.8635 | -21.9 | 1123 | 46.7917 | 297.6198 | 744413.2961
| 1124 | -21.8635 | 297.2406 | -21.8866 | -21.9 | 1124 | 46.8333 | 297.2406 | 744710.5367
| 1125 | -21.8866 | 296.862 | -21.9096 | -21.9 | 1125 | 46.875 | 296.862 | 745007.3987
| 1126 | -21.9096 | 296.4838 | -21.9327 | -21.9 | 1126 | 46.9167 | 296.4838 | 745303.8825
| 1127 | -21.9327 | 296.1061 | -21.9557 | -22 | 1127 | 46.9583 | 296.1061 | 745599.9886
| 1128 | -21.9557 | 295.7289 | -21.9787 | -22 | 1128 | 47 | 295.7289 | 745895.7175
| 1129 | -21.9787 | 295.3521 | -22.0016 | -22 | 1129 | 47.0417 | 295.3521 | 746191.0697
| 1130 | -22.0016 | 294.9759 | -22.0246 | -22 | 1130 | 47.0833 | 294.9759 | 746486.0455
| 1131 | -22.0246 | 294.6001 | -22.0475 | -22 | 1131 | 47.125 | 294.6001 | 746780.6457
| 1132 | -22.0475 | 294.2248 | -22.0703 | -22.1 | 1132 | 47.1667 | 294.2248 | 747074.8705
| 1133 | -22.0703 | 293.85 | -22.0932 | -22.1 | 1133 | 47.2083 | 293.85 | 747368.7205
| 1134 | -22.0932 | 293.4757 | -22.116 | -22.1 | 1134 | 47.25 | 293.4757 | 747662.1961
| 1135 | -22.116 | 293.1018 | -22.1388 | -22.1 | 1135 | 47.2917 | 293.1018 | 747955.2979
| 1136 | -22.1388 | 292.7284 | -22.1615 | -22.2 | 1136 | 47.3333 | 292.7284 | 748248.0263
| 1137 | -22.1615 | 292.3555 | -22.1843 | -22.2 | 1137 | 47.375 | 292.3555 | 748540.3818
| 1138 | -22.1843 | 291.983 | -22.2069 | -22.2 | 1138 | 47.4167 | 291.983 | 748832.3648
| 1139 | -22.2069 | 291.6111 | -22.2296 | -22.2 | 1139 | 47.4583 | 291.6111 | 749123.9759
| 1140 | -22.2296 | 291.2396 | -22.2523 | -22.3 | 1140 | 47.5 | 291.2396 | 749415.2155
| 1141 | -22.2523 | 290.8686 | -22.2749 | -22.3 | 1141 | 47.5417 | 290.8686 | 749706.0841
| 1142 | -22.2749 | 290.498 | -22.2974 | -22.3 | 1142 | 47.5833 | 290.498 | 749996.5821
| 1143 | -22.2974 | 290.128 | -22.32 | -22.3 | 1143 | 47.625 | 290.128 | 750286.7101
| 1144 | -22.32 | 289.7584 | -22.3425 | -22.3 | 1144 | 47.6667 | 289.7584 | 750576.4684
| 1145 | -22.3425 | 289.3892 | -22.365 | -22.4 | 1145 | 47.7083 | 289.3892 | 750865.8577
| 1146 | -22.365 | 289.0206 | -22.3875 | -22.4 | 1146 | 47.75 | 289.0206 | 751154.8782
| 1147 | -22.3875 | 288.6524 | -22.4099 | -22.4 | 1147 | 47.7917 | 288.6524 | 751443.5306
| 1148 | -22.4099 | 288.2847 | -22.4323 | -22.4 | 1148 | 47.8333 | 288.2847 | 751731.8152
| 1149 | -22.4323 | 287.9174 | -22.4547 | -22.5 | 1149 | 47.875 | 287.9174 | 752019.7326
| 1150 | -22.4547 | 287.5506 | -22.4771 | -22.5 | 1150 | 47.9167 | 287.5506 | 752307.2833
| 1151 | -22.4771 | 287.1843 | -22.4994 | -22.5 | 1151 | 47.9583 | 287.1843 | 752594.4676
| 1152 | -22.4994 | 286.8184 | -22.5217 | -22.5 | 1152 | 48 | 286.8184 | 752881.286
| 1153 | -22.5217 | 286.4531 | -22.5439 | -22.5 | 1153 | 48.0417 | 286.4531 | 753167.7391
| 1154 | -22.5439 | 286.0881 | -22.5662 | -22.6 | 1154 | 48.0833 | 286.0881 | 753453.8272
| 1155 | -22.5662 | 285.7237 | -22.5884 | -22.6 | 1155 | 48.125 | 285.7237 | 753739.5509
| 1156 | -22.5884 | 285.3597 | -22.6106 | -22.6 | 1156 | 48.1667 | 285.3597 | 754024.9106
| 1157 | -22.6106 | 284.9962 | -22.6327 | -22.6 | 1157 | 48.2083 | 284.9962 | 754309.9067
| 1158 | -22.6327 | 284.6331 | -22.6548 | -22.7 | 1158 | 48.25 | 284.6331 | 754594.5399
| 1159 | -22.6548 | 284.2705 | -22.6769 | -22.7 | 1159 | 48.2917 | 284.2705 | 754878.8104
| 1160 | -22.6769 | 283.9084 | -22.699 | -22.7 | 1160 | 48.3333 | 283.9084 | 755162.7187
| 1161 | -22.699 | 283.5467 | -22.721 | -22.7 | 1161 | 48.375 | 283.5467 | 755446.2654
| 1162 | -22.721 | 283.1855 | -22.7431 | -22.7 | 1162 | 48.4167 | 283.1855 | 755729.4509
| 1163 | -22.7431 | 282.8247 | -22.765 | -22.8 | 1163 | 48.4583 | 282.8247 | 756012.2756
| 1164 | -22.765 | 282.4644 | -22.787 | -22.8 | 1164 | 48.5 | 282.4644 | 756294.74
| 1165 | -22.787 | 282.1046 | -22.8089 | -22.8 | 1165 | 48.5417 | 282.1046 | 756576.8446
| 1166 | -22.8089 | 281.7452 | -22.8308 | -22.8 | 1166 | 48.5833 | 281.7452 | 756858.5898
| 1167 | -22.8308 | 281.3863 | -22.8527 | -22.9 | 1167 | 48.625 | 281.3863 | 757139.9761
| 1168 | -22.8527 | 281.0278 | -22.8745 | -22.9 | 1168 | 48.6667 | 281.0278 | 757421.0039
| 1169 | -22.8745 | 280.6698 | -22.8964 | -22.9 | 1169 | 48.7083 | 280.6698 | 757701.6737
| 1170 | -22.8964 | 280.3122 | -22.9181 | -22.9 | 1170 | 48.75 | 280.3122 | 757981.9859
| 1171 | -22.9181 | 279.9552 | -22.9399 | -22.9 | 1171 | 48.7917 | 279.9552 | 758261.9411
| 1172 | -22.9399 | 279.5985 | -22.9616 | -23 | 1172 | 48.8333 | 279.5985 | 758541.5396
| 1173 | -22.9616 | 279.2423 | -22.9833 | -23 | 1173 | 48.875 | 279.2423 | 758820.7819
| 1174 | -22.9833 | 278.8866 | -23.005 | -23 | 1174 | 48.9167 | 278.8866 | 759099.6685
| 1175 | -23.005 | 278.5313 | -23.0267 | -23 | 1175 | 48.9583 | 278.5313 | 759378.1998
| 1176 | -23.0267 | 278.1765 | -23.0483 | -23 | 1176 | 49 | 278.1765 | 759656.3763
| 1177 | -23.0483 | 277.8221 | -23.0699 | -23.1 | 1177 | 49.0417 | 277.8221 | 759934.1984
| 1178 | -23.0699 | 277.4682 | -23.0915 | -23.1 | 1178 | 49.0833 | 277.4682 | 760211.6666
| 1179 | -23.0915 | 277.1147 | -23.113 | -23.1 | 1179 | 49.125 | 277.1147 | 760488.7813
| 1180 | -23.113 | 276.7617 | -23.1345 | -23.1 | 1180 | 49.1667 | 276.7617 | 760765.543
| 1181 | -23.1345 | 276.4091 | -23.156 | -23.2 | 1181 | 49.2083 | 276.4091 | 761041.9521
| 1182 | -23.156 | 276.057 | -23.1775 | -23.2 | 1182 | 49.25 | 276.057 | 761318.0091
| 1183 | -23.1775 | 275.7053 | -23.1989 | -23.2 | 1183 | 49.2917 | 275.7053 | 761593.7144
| 1184 | -23.1989 | 275.3541 | -23.2203 | -23.2 | 1184 | 49.3333 | 275.3541 | 761869.0685
| 1185 | -23.2203 | 275.0033 | -23.2417 | -23.2 | 1185 | 49.375 | 275.0033 | 762144.0718
| 1186 | -23.2417 | 274.653 | -23.263 | -23.3 | 1186 | 49.4167 | 274.653 | 762418.7247
| 1187 | -23.263 | 274.3031 | -23.2843 | -23.3 | 1187 | 49.4583 | 274.3031 | 762693.0278
| 1188 | -23.2843 | 273.9536 | -23.3056 | -23.3 | 1188 | 49.5 | 273.9536 | 762966.9815
| 1189 | -23.3056 | 273.6046 | -23.3269 | -23.3 | 1189 | 49.5417 | 273.6046 | 763240.5861
| 1190 | -23.3269 | 273.2561 | -23.3481 | -23.3 | 1190 | 49.5833 | 273.2561 | 763513.8422
| 1191 | -23.3481 | 272.908 | -23.3694 | -23.4 | 1191 | 49.625 | 272.908 | 763786.7502
| 1192 | -23.3694 | 272.5603 | -23.3905 | -23.4 | 1192 | 49.6667 | 272.5603 | 764059.3105
| 1193 | -23.3905 | 272.2131 | -23.4117 | -23.4 | 1193 | 49.7083 | 272.2131 | 764331.5236
| 1194 | -23.4117 | 271.8663 | -23.4328 | -23.4 | 1194 | 49.75 | 271.8663 | 764603.3899
| 1195 | -23.4328 | 271.52 | -23.4539 | -23.5 | 1195 | 49.7917 | 271.52 | 764874.9099
| 1196 | -23.4539 | 271.1741 | -23.475 | -23.5 | 1196 | 49.8333 | 271.1741 | 765146.084
| 1197 | -23.475 | 270.8286 | -23.4961 | -23.5 | 1197 | 49.875 | 270.8286 | 765416.9126
| 1198 | -23.4961 | 270.4836 | -23.5171 | -23.5 | 1198 | 49.9167 | 270.4836 | 765687.3962
| 1199 | -23.5171 | 270.139 | -23.5381 | -23.5 | 1199 | 49.9583 | 270.139 | 765957.5353
| 1200 | -23.5381 | 269.7949 | -23.5591 | -23.6 | 1200 | 50 | 269.7949 | 766227.3302
| 1201 | -23.5591 | 269.4512 | -23.58 | -23.6 | 1201 | 50.0417 | 269.4512 | 766496.7814
| 1202 | -23.58 | 269.1079 | -23.6009 | -23.6 | 1202 | 50.0833 | 269.1079 | 766765.8893
| 1203 | -23.6009 | 268.7651 | -23.6218 | -23.6 | 1203 | 50.125 | 268.7651 | 767034.6545
| 1204 | -23.6218 | 268.4227 | -23.6427 | -23.6 | 1204 | 50.1667 | 268.4227 | 767303.0772
| 1205 | -23.6427 | 268.0808 | -23.6635 | -23.7 | 1205 | 50.2083 | 268.0808 | 767571.158
| 1206 | -23.6635 | 267.7393 | -23.6843 | -23.7 | 1206 | 50.25 | 267.7393 | 767838.8972
| 1207 | -23.6843 | 267.3982 | -23.7051 | -23.7 | 1207 | 50.2917 | 267.3982 | 768106.2954
| 1208 | -23.7051 | 267.0575 | -23.7259 | -23.7 | 1208 | 50.3333 | 267.0575 | 768373.353
| 1209 | -23.7259 | 266.7173 | -23.7466 | -23.7 | 1209 | 50.375 | 266.7173 | 768640.0703
| 1210 | -23.7466 | 266.3776 | -23.7673 | -23.8 | 1210 | 50.4167 | 266.3776 | 768906.4479
| 1211 | -23.7673 | 266.0382 | -23.788 | -23.8 | 1211 | 50.4583 | 266.0382 | 769172.4861
| 1212 | -23.788 | 265.6993 | -23.8086 | -23.8 | 1212 | 50.5 | 265.6993 | 769438.1854
| 1213 | -23.8086 | 265.3608 | -23.8293 | -23.8 | 1213 | 50.5417 | 265.3608 | 769703.5462
| 1214 | -23.8293 | 265.0228 | -23.8499 | -23.8 | 1214 | 50.5833 | 265.0228 | 769968.569
| 1215 | -23.8499 | 264.6851 | -23.8704 | -23.9 | 1215 | 50.625 | 264.6851 | 770233.2541
| 1216 | -23.8704 | 264.348 | -23.891 | -23.9 | 1216 | 50.6667 | 264.348 | 770497.6021
| 1217 | -23.891 | 264.0112 | -23.9115 | -23.9 | 1217 | 50.7083 | 264.0112 | 770761.6133
| 1218 | -23.9115 | 263.6749 | -23.932 | -23.9 | 1218 | 50.75 | 263.6749 | 771025.2881
| 1219 | -23.932 | 263.339 | -23.9525 | -24 | 1219 | 50.7917 | 263.339 | 771288.6271
| 1220 | -23.9525 | 263.0035 | -23.9729 | -24 | 1220 | 50.8333 | 263.0035 | 771551.6306
| 1221 | -23.9729 | 262.6684 | -23.9933 | -24 | 1221 | 50.875 | 262.6684 | 771814.2991
| 1222 | -23.9933 | 262.3338 | -24.0137 | -24 | 1222 | 50.9167 | 262.3338 | 772076.6329
| 1223 | -24.0137 | 261.9996 | -24.0341 | -24 | 1223 | 50.9583 | 261.9996 | 772338.6325
| 1224 | -24.0341 | 261.6659 | -24.0544 | -24.1 | 1224 | 51 | 261.6659 | 772600.2984
| 1225 | -24.0544 | 261.3325 | -24.0747 | -24.1 | 1225 | 51.0417 | 261.3325 | 772861.6309
| 1226 | -24.0747 | 260.9996 | -24.095 | -24.1 | 1226 | 51.0833 | 260.9996 | 773122.6305
| 1227 | -24.095 | 260.6671 | -24.1153 | -24.1 | 1227 | 51.125 | 260.6671 | 773383.2976
| 1228 | -24.1153 | 260.335 | -24.1355 | -24.1 | 1228 | 51.1667 | 260.335 | 773643.6327
| 1229 | -24.1355 | 260.0034 | -24.1557 | -24.2 | 1229 | 51.2083 | 260.0034 | 773903.6361
| 1230 | -24.1557 | 259.6722 | -24.1759 | -24.2 | 1230 | 51.25 | 259.6722 | 774163.3082
| 1231 | -24.1759 | 259.3414 | -24.1961 | -24.2 | 1231 | 51.2917 | 259.3414 | 774422.6496
| 1232 | -24.1961 | 259.011 | -24.2162 | -24.2 | 1232 | 51.3333 | 259.011 | 774681.6606
| 1233 | -24.2162 | 258.681 | -24.2363 | -24.2 | 1233 | 51.375 | 258.681 | 774940.3416
| 1234 | -24.2363 | 258.3515 | -24.2564 | -24.3 | 1234 | 51.4167 | 258.3515 | 775198.6931
| 1235 | -24.2564 | 258.0224 | -24.2765 | -24.3 | 1235 | 51.4583 | 258.0224 | 775456.7155
| 1236 | -24.2765 | 257.6937 | -24.2965 | -24.3 | 1236 | 51.5 | 257.6937 | 775714.4091
| 1237 | -24.2965 | 257.3654 | -24.3165 | -24.3 | 1237 | 51.5417 | 257.3654 | 775971.7745
| 1238 | -24.3165 | 257.0375 | -24.3365 | -24.3 | 1238 | 51.5833 | 257.0375 | 776228.812
| 1239 | -24.3365 | 256.7101 | -24.3564 | -24.4 | 1239 | 51.625 | 256.7101 | 776485.5221
| 1240 | -24.3564 | 256.383 | -24.3764 | -24.4 | 1240 | 51.6667 | 256.383 | 776741.9051
| 1241 | -24.3764 | 256.0564 | -24.3963 | -24.4 | 1241 | 51.7083 | 256.0564 | 776997.9616
| 1242 | -24.3963 | 255.7302 | -24.4161 | -24.4 | 1242 | 51.75 | 255.7302 | 777253.6918
| 1243 | -24.4161 | 255.4045 | -24.436 | -24.4 | 1243 | 51.7917 | 255.4045 | 777509.0963
| 1244 | -24.436 | 255.0791 | -24.4558 | -24.5 | 1244 | 51.8333 | 255.0791 | 777764.1753
| 1245 | -24.4558 | 254.7541 | -24.4756 | -24.5 | 1245 | 51.875 | 254.7541 | 778018.9295
| 1246 | -24.4756 | 254.4296 | -24.4954 | -24.5 | 1246 | 51.9167 | 254.4296 | 778273.3591
| 1247 | -24.4954 | 254.1055 | -24.5152 | -24.5 | 1247 | 51.9583 | 254.1055 | 778527.4645
| 1248 | -24.5152 | 253.7818 | -24.5349 | -24.5 | 1248 | 52 | 253.7818 | 778781.2463
| 1249 | -24.5349 | 253.4585 | -24.5546 | -24.6 | 1249 | 52.0417 | 253.4585 | 779034.7048
| 1250 | -24.5546 | 253.1356 | -24.5743 | -24.6 | 1250 | 52.0833 | 253.1356 | 779287.8403
| 1251 | -24.5743 | 252.8131 | -24.5939 | -24.6 | 1251 | 52.125 | 252.8131 | 779540.6534
| 1252 | -24.5939 | 252.491 | -24.6135 | -24.6 | 1252 | 52.1667 | 252.491 | 779793.1445
| 1253 | -24.6135 | 252.1694 | -24.6331 | -24.6 | 1253 | 52.2083 | 252.1694 | 780045.3139
| 1254 | -24.6331 | 251.8481 | -24.6527 | -24.7 | 1254 | 52.25 | 251.8481 | 780297.162
| 1255 | -24.6527 | 251.5273 | -24.6723 | -24.7 | 1255 | 52.2917 | 251.5273 | 780548.6893
| 1256 | -24.6723 | 251.2069 | -24.6918 | -24.7 | 1256 | 52.3333 | 251.2069 | 780799.8962
| 1257 | -24.6918 | 250.8869 | -24.7113 | -24.7 | 1257 | 52.375 | 250.8869 | 781050.783
| 1258 | -24.7113 | 250.5672 | -24.7308 | -24.7 | 1258 | 52.4167 | 250.5672 | 781301.3503
| 1259 | -24.7308 | 250.248 | -24.7502 | -24.8 | 1259 | 52.4583 | 250.248 | 781551.5983
| 1260 | -24.7502 | 249.9292 | -24.7696 | -24.8 | 1260 | 52.5 | 249.9292 | 781801.5275
| 1261 | -24.7696 | 249.6109 | -24.7891 | -24.8 | 1261 | 52.5417 | 249.6109 | 782051.1384
| 1262 | -24.7891 | 249.2929 | -24.8084 | -24.8 | 1262 | 52.5833 | 249.2929 | 782300.4313
| 1263 | -24.8084 | 248.9753 | -24.8278 | -24.8 | 1263 | 52.625 | 248.9753 | 782549.4066
| 1264 | -24.8278 | 248.6581 | -24.8471 | -24.8 | 1264 | 52.6667 | 248.6581 | 782798.0647
| 1265 | -24.8471 | 248.3413 | -24.8664 | -24.9 | 1265 | 52.7083 | 248.3413 | 783046.406
| 1266 | -24.8664 | 248.025 | -24.8857 | -24.9 | 1266 | 52.75 | 248.025 | 783294.431
| 1267 | -24.8857 | 247.709 | -24.9049 | -24.9 | 1267 | 52.7917 | 247.709 | 783542.14
| 1268 | -24.9049 | 247.3934 | -24.9242 | -24.9 | 1268 | 52.8333 | 247.3934 | 783789.5334
| 1269 | -24.9242 | 247.0783 | -24.9434 | -24.9 | 1269 | 52.875 | 247.0783 | 784036.6117
| 1270 | -24.9434 | 246.7635 | -24.9626 | -25 | 1270 | 52.9167 | 246.7635 | 784283.3752
| 1271 | -24.9626 | 246.4492 | -24.9817 | -25 | 1271 | 52.9583 | 246.4492 | 784529.8244
| 1272 | -24.9817 | 246.1352 | -25.0009 | -25 | 1272 | 53 | 246.1352 | 784775.9596
| 1273 | -25.0009 | 245.8216 | -25.02 | -25 | 1273 | 53.0417 | 245.8216 | 785021.7812
| 1274 | -25.02 | 245.5085 | -25.039 | -25 | 1274 | 53.0833 | 245.5085 | 785267.2897
| 1275 | -25.039 | 245.1957 | -25.0581 | -25.1 | 1275 | 53.125 | 245.1957 | 785512.4855
| 1276 | -25.0581 | 244.8834 | -25.0771 | -25.1 | 1276 | 53.1667 | 244.8834 | 785757.3688
| 1277 | -25.0771 | 244.5714 | -25.0961 | -25.1 | 1277 | 53.2083 | 244.5714 | 786001.9402
| 1278 | -25.0961 | 244.2598 | -25.1151 | -25.1 | 1278 | 53.25 | 244.2598 | 786246.2001
| 1279 | -25.1151 | 243.9487 | -25.1341 | -25.1 | 1279 | 53.2917 | 243.9487 | 786490.1488
| 1280 | -25.1341 | 243.6379 | -25.153 | -25.2 | 1280 | 53.3333 | 243.6379 | 786733.7867
| 1281 | -25.153 | 243.3275 | -25.1719 | -25.2 | 1281 | 53.375 | 243.3275 | 786977.1142
| 1282 | -25.1719 | 243.0175 | -25.1908 | -25.2 | 1282 | 53.4167 | 243.0175 | 787220.1317
| 1283 | -25.1908 | 242.708 | -25.2097 | -25.2 | 1283 | 53.4583 | 242.708 | 787462.8397
| 1284 | -25.2097 | 242.3988 | -25.2285 | -25.2 | 1284 | 53.5 | 242.3988 | 787705.2385
| 1285 | -25.2285 | 242.09 | -25.2474 | -25.2 | 1285 | 53.5417 | 242.09 | 787947.3284
| 1286 | -25.2474 | 241.7816 | -25.2662 | -25.3 | 1286 | 53.5833 | 241.7816 | 788189.11
| 1287 | -25.2662 | 241.4736 | -25.2849 | -25.3 | 1287 | 53.625 | 241.4736 | 788430.5835
| 1288 | -25.2849 | 241.1659 | -25.3037 | -25.3 | 1288 | 53.6667 | 241.1659 | 788671.7495
| 1289 | -25.3037 | 240.8587 | -25.3224 | -25.3 | 1289 | 53.7083 | 240.8587 | 788912.6082
| 1290 | -25.3224 | 240.5519 | -25.3411 | -25.3 | 1290 | 53.75 | 240.5519 | 789153.1601
| 1291 | -25.3411 | 240.2454 | -25.3598 | -25.4 | 1291 | 53.7917 | 240.2454 | 789393.4055
| 1292 | -25.3598 | 239.9394 | -25.3784 | -25.4 | 1292 | 53.8333 | 239.9394 | 789633.3448
| 1293 | -25.3784 | 239.6337 | -25.397 | -25.4 | 1293 | 53.875 | 239.6337 | 789872.9786
| 1294 | -25.397 | 239.3284 | -25.4156 | -25.4 | 1294 | 53.9167 | 239.3284 | 790112.307
| 1295 | -25.4156 | 239.0235 | -25.4342 | -25.4 | 1295 | 53.9583 | 239.0235 | 790351.3305
| 1296 | -25.4342 | 238.719 | -25.4528 | -25.5 | 1296 | 54 | 238.719 | 790590.0496
| 1297 | -25.4528 | 238.4149 | -25.4713 | -25.5 | 1297 | 54.0417 | 238.4149 | 790828.4645
| 1298 | -25.4713 | 238.1112 | -25.4898 | -25.5 | 1298 | 54.0833 | 238.1112 | 791066.5757
| 1299 | -25.4898 | 237.8079 | -25.5083 | -25.5 | 1299 | 54.125 | 237.8079 | 791304.3836
| 1300 | -25.5083 | 237.5049 | -25.5268 | -25.5 | 1300 | 54.1667 | 237.5049 | 791541.8885
| 1301 | -25.5268 | 237.2024 | -25.5452 | -25.5 | 1301 | 54.2083 | 237.2024 | 791779.0909
| 1302 | -25.5452 | 236.9002 | -25.5636 | -25.6 | 1302 | 54.25 | 236.9002 | 792015.9911
| 1303 | -25.5636 | 236.5984 | -25.582 | -25.6 | 1303 | 54.2917 | 236.5984 | 792252.5895
| 1304 | -25.582 | 236.297 | -25.6004 | -25.6 | 1304 | 54.3333 | 236.297 | 792488.8865
| 1305 | -25.6004 | 235.996 | -25.6187 | -25.6 | 1305 | 54.375 | 235.996 | 792724.8824
| 1306 | -25.6187 | 235.6953 | -25.637 | -25.6 | 1306 | 54.4167 | 235.6953 | 792960.5778
| 1307 | -25.637 | 235.3951 | -25.6553 | -25.7 | 1307 | 54.4583 | 235.3951 | 793195.9728
| 1308 | -25.6553 | 235.0952 | -25.6736 | -25.7 | 1308 | 54.5 | 235.0952 | 793431.068
| 1309 | -25.6736 | 234.7957 | -25.6919 | -25.7 | 1309 | 54.5417 | 234.7957 | 793665.8637
| 1310 | -25.6919 | 234.4966 | -25.7101 | -25.7 | 1310 | 54.5833 | 234.4966 | 793900.3603
| 1311 | -25.7101 | 234.1979 | -25.7283 | -25.7 | 1311 | 54.625 | 234.1979 | 794134.5581
| 1312 | -25.7283 | 233.8995 | -25.7465 | -25.7 | 1312 | 54.6667 | 233.8995 | 794368.4576
| 1313 | -25.7465 | 233.6015 | -25.7646 | -25.8 | 1313 | 54.7083 | 233.6015 | 794602.0592
| 1314 | -25.7646 | 233.3039 | -25.7828 | -25.8 | 1314 | 54.75 | 233.3039 | 794835.3631
| 1315 | -25.7828 | 233.0067 | -25.8009 | -25.8 | 1315 | 54.7917 | 233.0067 | 795068.3698
| 1316 | -25.8009 | 232.7099 | -25.819 | -25.8 | 1316 | 54.8333 | 232.7099 | 795301.0797
| 1317 | -25.819 | 232.4134 | -25.837 | -25.8 | 1317 | 54.875 | 232.4134 | 795533.4932
| 1318 | -25.837 | 232.1174 | -25.8551 | -25.9 | 1318 | 54.9167 | 232.1174 | 795765.6105
| 1319 | -25.8551 | 231.8217 | -25.8731 | -25.9 | 1319 | 54.9583 | 231.8217 | 795997.4322
| 1320 | -25.8731 | 231.5263 | -25.8911 | -25.9 | 1320 | 55 | 231.5263 | 796228.9585
| 1321 | -25.8911 | 231.2314 | -25.9091 | -25.9 | 1321 | 55.0417 | 231.2314 | 796460.1899
| 1322 | -25.9091 | 230.9368 | -25.927 | -25.9 | 1322 | 55.0833 | 230.9368 | 796691.1267
| 1323 | -25.927 | 230.6426 | -25.9449 | -25.9 | 1323 | 55.125 | 230.6426 | 796921.7693
| 1324 | -25.9449 | 230.3488 | -25.9629 | -26 | 1324 | 55.1667 | 230.3488 | 797152.1182
| 1325 | -25.9629 | 230.0554 | -25.9807 | -26 | 1325 | 55.2083 | 230.0554 | 797382.1735
| 1326 | -25.9807 | 229.7623 | -25.9986 | -26 | 1326 | 55.25 | 229.7623 | 797611.9358
| 1327 | -25.9986 | 229.4696 | -26.0164 | -26 | 1327 | 55.2917 | 229.4696 | 797841.4054
| 1328 | -26.0164 | 229.1773 | -26.0342 | -26 | 1328 | 55.3333 | 229.1773 | 798070.5826
| 1329 | -26.0342 | 228.8853 | -26.052 | -26.1 | 1329 | 55.375 | 228.8853 | 798299.4679
| 1330 | -26.052 | 228.5937 | -26.0698 | -26.1 | 1330 | 55.4167 | 228.5937 | 798528.0616
| 1331 | -26.0698 | 228.3025 | -26.0876 | -26.1 | 1331 | 55.4583 | 228.3025 | 798756.3642
| 1332 | -26.0876 | 228.0117 | -26.1053 | -26.1 | 1332 | 55.5 | 228.0117 | 798984.3758
| 1333 | -26.1053 | 227.7212 | -26.123 | -26.1 | 1333 | 55.5417 | 227.7212 | 799212.097
| 1334 | -26.123 | 227.4311 | -26.1407 | -26.1 | 1334 | 55.5833 | 227.4311 | 799439.5281
| 1335 | -26.1407 | 227.1414 | -26.1583 | -26.2 | 1335 | 55.625 | 227.1414 | 799666.6695
| 1336 | -26.1583 | 226.852 | -26.1759 | -26.2 | 1336 | 55.6667 | 226.852 | 799893.5215
| 1337 | -26.1759 | 226.563 | -26.1936 | -26.2 | 1337 | 55.7083 | 226.563 | 800120.0845
| 1338 | -26.1936 | 226.2744 | -26.2111 | -26.2 | 1338 | 55.75 | 226.2744 | 800346.3589
| 1339 | -26.2111 | 225.9861 | -26.2287 | -26.2 | 1339 | 55.7917 | 225.9861 | 800572.345
| 1340 | -26.2287 | 225.6982 | -26.2463 | -26.2 | 1340 | 55.8333 | 225.6982 | 800798.0433
| 1341 | -26.2463 | 225.4107 | -26.2638 | -26.3 | 1341 | 55.875 | 225.4107 | 801023.454
| 1342 | -26.2638 | 225.1236 | -26.2813 | -26.3 | 1342 | 55.9167 | 225.1236 | 801248.5776
| 1343 | -26.2813 | 224.8368 | -26.2987 | -26.3 | 1343 | 55.9583 | 224.8368 | 801473.4143
| 1344 | -26.2987 | 224.5503 | -26.3162 | -26.3 | 1344 | 56 | 224.5503 | 801697.9647
| 1345 | -26.3162 | 224.2643 | -26.3336 | -26.3 | 1345 | 56.0417 | 224.2643 | 801922.229
| 1346 | -26.3336 | 223.9786 | -26.351 | -26.4 | 1346 | 56.0833 | 223.9786 | 802146.2076
| 1347 | -26.351 | 223.6933 | -26.3684 | -26.4 | 1347 | 56.125 | 223.6933 | 802369.9008
| 1348 | -26.3684 | 223.4083 | -26.3858 | -26.4 | 1348 | 56.1667 | 223.4083 | 802593.3091
| 1349 | -26.3858 | 223.1237 | -26.4031 | -26.4 | 1349 | 56.2083 | 223.1237 | 802816.4328
| 1350 | -26.4031 | 222.8394 | -26.4205 | -26.4 | 1350 | 56.25 | 222.8394 | 803039.2723
| 1351 | -26.4205 | 222.5556 | -26.4378 | -26.4 | 1351 | 56.2917 | 222.5556 | 803261.8278
| 1352 | -26.4378 | 222.272 | -26.455 | -26.5 | 1352 | 56.3333 | 222.272 | 803484.0999
| 1353 | -26.455 | 221.9889 | -26.4723 | -26.5 | 1353 | 56.375 | 221.9889 | 803706.0888
| 1354 | -26.4723 | 221.7061 | -26.4895 | -26.5 | 1354 | 56.4167 | 221.7061 | 803927.7948
| 1355 | -26.4895 | 221.4237 | -26.5067 | -26.5 | 1355 | 56.4583 | 221.4237 | 804149.2185
| 1356 | -26.5067 | 221.1416 | -26.5239 | -26.5 | 1356 | 56.5 | 221.1416 | 804370.3601
| 1357 | -26.5239 | 220.8599 | -26.5411 | -26.5 | 1357 | 56.5417 | 220.8599 | 804591.2199
| 1358 | -26.5411 | 220.5785 | -26.5582 | -26.6 | 1358 | 56.5833 | 220.5785 | 804811.7984
| 1359 | -26.5582 | 220.2975 | -26.5754 | -26.6 | 1359 | 56.625 | 220.2975 | 805032.0959
| 1360 | -26.5754 | 220.0169 | -26.5925 | -26.6 | 1360 | 56.6667 | 220.0169 | 805252.1128
| 1361 | -26.5925 | 219.7366 | -26.6095 | -26.6 | 1361 | 56.7083 | 219.7366 | 805471.8494
| 1362 | -26.6095 | 219.4566 | -26.6266 | -26.6 | 1362 | 56.75 | 219.4566 | 805691.306
| 1363 | -26.6266 | 219.1771 | -26.6436 | -26.6 | 1363 | 56.7917 | 219.1771 | 805910.4831
| 1364 | -26.6436 | 218.8979 | -26.6607 | -26.7 | 1364 | 56.8333 | 218.8979 | 806129.3809
| 1365 | -26.6607 | 218.619 | -26.6777 | -26.7 | 1365 | 56.875 | 218.619 | 806347.9999
| 1366 | -26.6777 | 218.3405 | -26.6946 | -26.7 | 1366 | 56.9167 | 218.3405 | 806566.3404
| 1367 | -26.6946 | 218.0623 | -26.7116 | -26.7 | 1367 | 56.9583 | 218.0623 | 806784.4028
| 1368 | -26.7116 | 217.7846 | -26.7285 | -26.7 | 1368 | 57 | 217.7846 | 807002.1873
| 1369 | -26.7285 | 217.5071 | -26.7454 | -26.7 | 1369 | 57.0417 | 217.5071 | 807219.6944
| 1370 | -26.7454 | 217.23 | -26.7623 | -26.8 | 1370 | 57.0833 | 217.23 | 807436.9245
| 1371 | -26.7623 | 216.9533 | -26.7792 | -26.8 | 1371 | 57.125 | 216.9533 | 807653.8778
| 1372 | -26.7792 | 216.6769 | -26.796 | -26.8 | 1372 | 57.1667 | 216.6769 | 807870.5547
| 1373 | -26.796 | 216.4009 | -26.8128 | -26.8 | 1373 | 57.2083 | 216.4009 | 808086.9555
| 1374 | -26.8128 | 216.1252 | -26.8296 | -26.8 | 1374 | 57.25 | 216.1252 | 808303.0807
| 1375 | -26.8296 | 215.8499 | -26.8464 | -26.8 | 1375 | 57.2917 | 215.8499 | 808518.9306
| 1376 | -26.8464 | 215.5749 | -26.8632 | -26.9 | 1376 | 57.3333 | 215.5749 | 808734.5055
| 1377 | -26.8632 | 215.3003 | -26.8799 | -26.9 | 1377 | 57.375 | 215.3003 | 808949.8058
| 1378 | -26.8799 | 215.026 | -26.8966 | -26.9 | 1378 | 57.4167 | 215.026 | 809164.8318
| 1379 | -26.8966 | 214.7521 | -26.9133 | -26.9 | 1379 | 57.4583 | 214.7521 | 809379.5838
| 1380 | -26.9133 | 214.4785 | -26.93 | -26.9 | 1380 | 57.5 | 214.4785 | 809594.0623
| 1381 | -26.93 | 214.2053 | -26.9466 | -26.9 | 1381 | 57.5417 | 214.2053 | 809808.2676
| 1382 | -26.9466 | 213.9324 | -26.9632 | -27 | 1382 | 57.5833 | 213.9324 | 810022.1999
| 1383 | -26.9632 | 213.6598 | -26.9799 | -27 | 1383 | 57.625 | 213.6598 | 810235.8598
| 1384 | -26.9799 | 213.3877 | -26.9964 | -27 | 1384 | 57.6667 | 213.3877 | 810449.2474
| 1385 | -26.9964 | 213.1158 | -27.013 | -27 | 1385 | 57.7083 | 213.1158 | 810662.3632
| 1386 | -27.013 | 212.8443 | -27.0296 | -27 | 1386 | 57.75 | 212.8443 | 810875.2076
| 1387 | -27.0296 | 212.5732 | -27.0461 | -27 | 1387 | 57.7917 | 212.5732 | 811087.7807
| 1388 | -27.0461 | 212.3024 | -27.0626 | -27.1 | 1388 | 57.8333 | 212.3024 | 811300.0831
| 1389 | -27.0626 | 212.0319 | -27.0791 | -27.1 | 1389 | 57.875 | 212.0319 | 811512.115
| 1390 | -27.0791 | 211.7618 | -27.0955 | -27.1 | 1390 | 57.9167 | 211.7618 | 811723.8768
| 1391 | -27.0955 | 211.492 | -27.112 | -27.1 | 1391 | 57.9583 | 211.492 | 811935.3689
| 1392 | -27.112 | 211.2226 | -27.1284 | -27.1 | 1392 | 58 | 211.2226 | 812146.5915
| 1393 | -27.1284 | 210.9535 | -27.1448 | -27.1 | 1393 | 58.0417 | 210.9535 | 812357.545
| 1394 | -27.1448 | 210.6848 | -27.1612 | -27.2 | 1394 | 58.0833 | 210.6848 | 812568.2298
| 1395 | -27.1612 | 210.4164 | -27.1775 | -27.2 | 1395 | 58.125 | 210.4164 | 812778.6462
| 1396 | -27.1775 | 210.1483 | -27.1938 | -27.2 | 1396 | 58.1667 | 210.1483 | 812988.7945
| 1397 | -27.1938 | 209.8806 | -27.2102 | -27.2 | 1397 | 58.2083 | 209.8806 | 813198.6751
| 1398 | -27.2102 | 209.6133 | -27.2265 | -27.2 | 1398 | 58.25 | 209.6133 | 813408.2884
| 1399 | -27.2265 | 209.3462 | -27.2427 | -27.2 | 1399 | 58.2917 | 209.3462 | 813617.6346
| 1400 | -27.2427 | 209.0795 | -27.259 | -27.3 | 1400 | 58.3333 | 209.0795 | 813826.7141
| 1401 | -27.259 | 208.8132 | -27.2752 | -27.3 | 1401 | 58.375 | 208.8132 | 814035.5273
| 1402 | -27.2752 | 208.5472 | -27.2914 | -27.3 | 1402 | 58.4167 | 208.5472 | 814244.0745
| 1403 | -27.2914 | 208.2815 | -27.3076 | -27.3 | 1403 | 58.4583 | 208.2815 | 814452.356
| 1404 | -27.3076 | 208.0162 | -27.3238 | -27.3 | 1404 | 58.5 | 208.0162 | 814660.3721
| 1405 | -27.3238 | 207.7512 | -27.3399 | -27.3 | 1405 | 58.5417 | 207.7512 | 814868.1233
| 1406 | -27.3399 | 207.4865 | -27.3561 | -27.4 | 1406 | 58.5833 | 207.4865 | 815075.6098
| 1407 | -27.3561 | 207.2222 | -27.3722 | -27.4 | 1407 | 58.625 | 207.2222 | 815282.832
| 1408 | -27.3722 | 206.9582 | -27.3882 | -27.4 | 1408 | 58.6667 | 206.9582 | 815489.7901
| 1409 | -27.3882 | 206.6945 | -27.4043 | -27.4 | 1409 | 58.7083 | 206.6945 | 815696.4847
| 1410 | -27.4043 | 206.4312 | -27.4204 | -27.4 | 1410 | 58.75 | 206.4312 | 815902.9159
| 1411 | -27.4204 | 206.1683 | -27.4364 | -27.4 | 1411 | 58.7917 | 206.1683 | 816109.0842
| 1412 | -27.4364 | 205.9056 | -27.4524 | -27.5 | 1412 | 58.8333 | 205.9056 | 816314.9898
| 1413 | -27.4524 | 205.6433 | -27.4684 | -27.5 | 1413 | 58.875 | 205.6433 | 816520.6331
| 1414 | -27.4684 | 205.3813 | -27.4843 | -27.5 | 1414 | 58.9167 | 205.3813 | 816726.0144
| 1415 | -27.4843 | 205.1197 | -27.5003 | -27.5 | 1415 | 58.9583 | 205.1197 | 816931.1341
| 1416 | -27.5003 | 204.8584 | -27.5162 | -27.5 | 1416 | 59 | 204.8584 | 817135.9925
| 1417 | -27.5162 | 204.5974 | -27.5321 | -27.5 | 1417 | 59.0417 | 204.5974 | 817340.5899
| 1418 | -27.5321 | 204.3368 | -27.548 | -27.5 | 1418 | 59.0833 | 204.3368 | 817544.9266
| 1419 | -27.548 | 204.0765 | -27.5639 | -27.6 | 1419 | 59.125 | 204.0765 | 817749.0031
| 1420 | -27.5639 | 203.8165 | -27.5797 | -27.6 | 1420 | 59.1667 | 203.8165 | 817952.8196
| 1421 | -27.5797 | 203.5568 | -27.5955 | -27.6 | 1421 | 59.2083 | 203.5568 | 818156.3764
| 1422 | -27.5955 | 203.2975 | -27.6113 | -27.6 | 1422 | 59.25 | 203.2975 | 818359.6739
| 1423 | -27.6113 | 203.0385 | -27.6271 | -27.6 | 1423 | 59.2917 | 203.0385 | 818562.7124
| 1424 | -27.6271 | 202.7799 | -27.6429 | -27.6 | 1424 | 59.3333 | 202.7799 | 818765.4923
| 1425 | -27.6429 | 202.5215 | -27.6586 | -27.7 | 1425 | 59.375 | 202.5215 | 818968.0139
| 1426 | -27.6586 | 202.2635 | -27.6743 | -27.7 | 1426 | 59.4167 | 202.2635 | 819170.2774
| 1427 | -27.6743 | 202.0059 | -27.69 | -27.7 | 1427 | 59.4583 | 202.0059 | 819372.2833
| 1428 | -27.69 | 201.7485 | -27.7057 | -27.7 | 1428 | 59.5 | 201.7485 | 819574.0318
| 1429 | -27.7057 | 201.4915 | -27.7214 | -27.7 | 1429 | 59.5417 | 201.4915 | 819775.5234
| 1430 | -27.7214 | 201.2348 | -27.737 | -27.7 | 1430 | 59.5833 | 201.2348 | 819976.7582
| 1431 | -27.737 | 200.9785 | -27.7526 | -27.8 | 1431 | 59.625 | 200.9785 | 820177.7367
| 1432 | -27.7526 | 200.7225 | -27.7682 | -27.8 | 1432 | 59.6667 | 200.7225 | 820378.4591
| 1433 | -27.7682 | 200.4667 | -27.7838 | -27.8 | 1433 | 59.7083 | 200.4667 | 820578.9259
| 1434 | -27.7838 | 200.2114 | -27.7994 | -27.8 | 1434 | 59.75 | 200.2114 | 820779.1372
| 1435 | -27.7994 | 199.9563 | -27.8149 | -27.8 | 1435 | 59.7917 | 199.9563 | 820979.0936
| 1436 | -27.8149 | 199.7016 | -27.8305 | -27.8 | 1436 | 59.8333 | 199.7016 | 821178.7951
| 1437 | -27.8305 | 199.4472 | -27.846 | -27.8 | 1437 | 59.875 | 199.4472 | 821378.2423
| 1438 | -27.846 | 199.1931 | -27.8614 | -27.9 | 1438 | 59.9167 | 199.1931 | 821577.4354
| 1439 | -27.8614 | 198.9393 | -27.8769 | -27.9 | 1439 | 59.9583 | 198.9393 | 821776.3748
| 1440 | -27.8769 | 198.6859 | -27.8923 | -27.9 | 1440 | 60 | 198.6859 | 821975.0607
| 1441 | -27.8923 | 198.4328 | -27.9078 | -27.9 | 1441 | 60.0417 | 198.4328 | 822173.4935
| 1442 | -27.9078 | 198.18 | -27.9232 | -27.9 | 1442 | 60.0833 | 198.18 | 822371.6735
| 1443 | -27.9232 | 197.9275 | -27.9386 | -27.9 | 1443 | 60.125 | 197.9275 | 822569.601
| 1444 | -27.9386 | 197.6754 | -27.9539 | -28 | 1444 | 60.1667 | 197.6754 | 822767.2764
| 1445 | -27.9539 | 197.4236 | -27.9693 | -28 | 1445 | 60.2083 | 197.4236 | 822964.7
| 1446 | -27.9693 | 197.1721 | -27.9846 | -28 | 1446 | 60.25 | 197.1721 | 823161.8721
| 1447 | -27.9846 | 196.9209 | -27.9999 | -28 | 1447 | 60.2917 | 196.9209 | 823358.793
| 1448 | -27.9999 | 196.67 | -28.0152 | -28 | 1448 | 60.3333 | 196.67 | 823555.463
| 1449 | -28.0152 | 196.4195 | -28.0305 | -28 | 1449 | 60.375 | 196.4195 | 823751.8825
| 1450 | -28.0305 | 196.1693 | -28.0457 | -28 | 1450 | 60.4167 | 196.1693 | 823948.0517
| 1451 | -28.0457 | 195.9194 | -28.0609 | -28.1 | 1451 | 60.4583 | 195.9194 | 824143.9711
| 1452 | -28.0609 | 195.6698 | -28.0761 | -28.1 | 1452 | 60.5 | 195.6698 | 824339.6408
| 1453 | -28.0761 | 195.4205 | -28.0913 | -28.1 | 1453 | 60.5417 | 195.4205 | 824535.0613
| 1454 | -28.0913 | 195.1715 | -28.1065 | -28.1 | 1454 | 60.5833 | 195.1715 | 824730.2329
| 1455 | -28.1065 | 194.9229 | -28.1217 | -28.1 | 1455 | 60.625 | 194.9229 | 824925.1558
| 1456 | -28.1217 | 194.6746 | -28.1368 | -28.1 | 1456 | 60.6667 | 194.6746 | 825119.8304
| 1457 | -28.1368 | 194.4266 | -28.1519 | -28.2 | 1457 | 60.7083 | 194.4266 | 825314.257
| 1458 | -28.1519 | 194.1789 | -28.167 | -28.2 | 1458 | 60.75 | 194.1789 | 825508.4359
| 1459 | -28.167 | 193.9315 | -28.1821 | -28.2 | 1459 | 60.7917 | 193.9315 | 825702.3675
| 1460 | -28.1821 | 193.6845 | -28.1971 | -28.2 | 1460 | 60.8333 | 193.6845 | 825896.052
| 1461 | -28.1971 | 193.4377 | -28.2122 | -28.2 | 1461 | 60.875 | 193.4377 | 826089.4897
| 1462 | -28.2122 | 193.1913 | -28.2272 | -28.2 | 1462 | 60.9167 | 193.1913 | 826282.681
| 1463 | -28.2272 | 192.9452 | -28.2422 | -28.2 | 1463 | 60.9583 | 192.9452 | 826475.6262
| 1464 | -28.2422 | 192.6994 | -28.2572 | -28.3 | 1464 | 61 | 192.6994 | 826668.3257
| 1465 | -28.2572 | 192.4539 | -28.2721 | -28.3 | 1465 | 61.0417 | 192.4539 | 826860.7796
| 1466 | -28.2721 | 192.2088 | -28.2871 | -28.3 | 1466 | 61.0833 | 192.2088 | 827052.9883
| 1467 | -28.2871 | 191.9639 | -28.302 | -28.3 | 1467 | 61.125 | 191.9639 | 827244.9522
| 1468 | -28.302 | 191.7194 | -28.3169 | -28.3 | 1468 | 61.1667 | 191.7194 | 827436.6716
| 1469 | -28.3169 | 191.4751 | -28.3318 | -28.3 | 1469 | 61.2083 | 191.4751 | 827628.1467
| 1470 | -28.3318 | 191.2312 | -28.3466 | -28.3 | 1470 | 61.25 | 191.2312 | 827819.3779
| 1471 | -28.3466 | 190.9876 | -28.3615 | -28.4 | 1471 | 61.2917 | 190.9876 | 828010.3655
| 1472 | -28.3615 | 190.7443 | -28.3763 | -28.4 | 1472 | 61.3333 | 190.7443 | 828201.1098
| 1473 | -28.3763 | 190.5013 | -28.3911 | -28.4 | 1473 | 61.375 | 190.5013 | 828391.611
| 1474 | -28.3911 | 190.2586 | -28.4059 | -28.4 | 1474 | 61.4167 | 190.2586 | 828581.8696
| 1475 | -28.4059 | 190.0162 | -28.4207 | -28.4 | 1475 | 61.4583 | 190.0162 | 828771.8859
| 1476 | -28.4207 | 189.7742 | -28.4354 | -28.4 | 1476 | 61.5 | 189.7742 | 828961.66
| 1477 | -28.4354 | 189.5324 | -28.4502 | -28.5 | 1477 | 61.5417 | 189.5324 | 829151.1924
| 1478 | -28.4502 | 189.2909 | -28.4649 | -28.5 | 1478 | 61.5833 | 189.2909 | 829340.4833
| 1479 | -28.4649 | 189.0498 | -28.4796 | -28.5 | 1479 | 61.625 | 189.0498 | 829529.5332
| 1480 | -28.4796 | 188.809 | -28.4942 | -28.5 | 1480 | 61.6667 | 188.809 | 829718.3421
| 1481 | -28.4942 | 188.5684 | -28.5089 | -28.5 | 1481 | 61.7083 | 188.5684 | 829906.9106
| 1482 | -28.5089 | 188.3282 | -28.5235 | -28.5 | 1482 | 61.75 | 188.3282 | 830095.2388
| 1483 | -28.5235 | 188.0883 | -28.5382 | -28.5 | 1483 | 61.7917 | 188.0883 | 830283.3271
| 1484 | -28.5382 | 187.8487 | -28.5528 | -28.6 | 1484 | 61.8333 | 187.8487 | 830471.1758
| 1485 | -28.5528 | 187.6094 | -28.5673 | -28.6 | 1485 | 61.875 | 187.6094 | 830658.7852
| 1486 | -28.5673 | 187.3704 | -28.5819 | -28.6 | 1486 | 61.9167 | 187.3704 | 830846.1555
| 1487 | -28.5819 | 187.1317 | -28.5964 | -28.6 | 1487 | 61.9583 | 187.1317 | 831033.2872
| 1488 | -28.5964 | 186.8933 | -28.611 | -28.6 | 1488 | 62 | 186.8933 | 831220.1805
| 1489 | -28.611 | 186.6552 | -28.6255 | -28.6 | 1489 | 62.0417 | 186.6552 | 831406.8357
| 1490 | -28.6255 | 186.4174 | -28.64 | -28.6 | 1490 | 62.0833 | 186.4174 | 831593.2532
| 1491 | -28.64 | 186.1799 | -28.6544 | -28.7 | 1491 | 62.125 | 186.1799 | 831779.4331
| 1492 | -28.6544 | 185.9428 | -28.6689 | -28.7 | 1492 | 62.1667 | 185.9428 | 831965.3759
| 1493 | -28.6689 | 185.7059 | -28.6833 | -28.7 | 1493 | 62.2083 | 185.7059 | 832151.0818
| 1494 | -28.6833 | 185.4693 | -28.6977 | -28.7 | 1494 | 62.25 | 185.4693 | 832336.5511
| 1495 | -28.6977 | 185.233 | -28.7121 | -28.7 | 1495 | 62.2917 | 185.233 | 832521.7841
| 1496 | -28.7121 | 184.9971 | -28.7265 | -28.7 | 1496 | 62.3333 | 184.9971 | 832706.7812
| 1497 | -28.7265 | 184.7614 | -28.7409 | -28.7 | 1497 | 62.375 | 184.7614 | 832891.5426
| 1498 | -28.7409 | 184.526 | -28.7552 | -28.8 | 1498 | 62.4167 | 184.526 | 833076.0686
| 1499 | -28.7552 | 184.2909 | -28.7696 | -28.8 | 1499 | 62.4583 | 184.2909 | 833260.3596
| 1500 | -28.7696 | 184.0562 | -28.7839 | -28.8 | 1500 | 62.5 | 184.0562 | 833444.4157
| 1501 | -28.7839 | 183.8217 | -28.7982 | -28.8 | 1501 | 62.5417 | 183.8217 | 833628.2374
| 1502 | -28.7982 | 183.5875 | -28.8124 | -28.8 | 1502 | 62.5833 | 183.5875 | 833811.825
| 1503 | -28.8124 | 183.3537 | -28.8267 | -28.8 | 1503 | 62.625 | 183.3537 | 833995.1786
| 1504 | -28.8267 | 183.1201 | -28.8409 | -28.8 | 1504 | 62.6667 | 183.1201 | 834178.2987
| 1505 | -28.8409 | 182.8868 | -28.8551 | -28.9 | 1505 | 62.7083 | 182.8868 | 834361.1855
| 1506 | -28.8551 | 182.6538 | -28.8693 | -28.9 | 1506 | 62.75 | 182.6538 | 834543.8393
| 1507 | -28.8693 | 182.4211 | -28.8835 | -28.9 | 1507 | 62.7917 | 182.4211 | 834726.2604
| 1508 | -28.8835 | 182.1887 | -28.8977 | -28.9 | 1508 | 62.8333 | 182.1887 | 834908.4491
| 1509 | -28.8977 | 181.9566 | -28.9118 | -28.9 | 1509 | 62.875 | 181.9566 | 835090.4058
| 1510 | -28.9118 | 181.7248 | -28.9259 | -28.9 | 1510 | 62.9167 | 181.7248 | 835272.1306
| 1511 | -28.9259 | 181.4933 | -28.94 | -28.9 | 1511 | 62.9583 | 181.4933 | 835453.6239
| 1512 | -28.94 | 181.2621 | -28.9541 | -29 | 1512 | 63 | 181.2621 | 835634.8861
| 1513 | -28.9541 | 181.0312 | -28.9682 | -29 | 1513 | 63.0417 | 181.0312 | 835815.9173
| 1514 | -28.9682 | 180.8006 | -28.9823 | -29 | 1514 | 63.0833 | 180.8006 | 835996.7179
| 1515 | -28.9823 | 180.5703 | -28.9963 | -29 | 1515 | 63.125 | 180.5703 | 836177.2881
| 1516 | -28.9963 | 180.3402 | -29.0103 | -29 | 1516 | 63.1667 | 180.3402 | 836357.6283
| 1517 | -29.0103 | 180.1105 | -29.0243 | -29 | 1517 | 63.2083 | 180.1105 | 836537.7388
| 1518 | -29.0243 | 179.881 | -29.0383 | -29 | 1518 | 63.25 | 179.881 | 836717.6199
| 1519 | -29.0383 | 179.6519 | -29.0523 | -29.1 | 1519 | 63.2917 | 179.6519 | 836897.2718
| 1520 | -29.0523 | 179.423 | -29.0662 | -29.1 | 1520 | 63.3333 | 179.423 | 837076.6948
| 1521 | -29.0662 | 179.1945 | -29.0801 | -29.1 | 1521 | 63.375 | 179.1945 | 837255.8892
| 1522 | -29.0801 | 178.9662 | -29.094 | -29.1 | 1522 | 63.4167 | 178.9662 | 837434.8554
| 1523 | -29.094 | 178.7382 | -29.1079 | -29.1 | 1523 | 63.4583 | 178.7382 | 837613.5936
| 1524 | -29.1079 | 178.5105 | -29.1218 | -29.1 | 1524 | 63.5 | 178.5105 | 837792.1041
| 1525 | -29.1218 | 178.2831 | -29.1357 | -29.1 | 1525 | 63.5417 | 178.2831 | 837970.3872
| 1526 | -29.1357 | 178.056 | -29.1495 | -29.1 | 1526 | 63.5833 | 178.056 | 838148.4431
| 1527 | -29.1495 | 177.8291 | -29.1633 | -29.2 | 1527 | 63.625 | 177.8291 | 838326.2722
| 1528 | -29.1633 | 177.6026 | -29.1771 | -29.2 | 1528 | 63.6667 | 177.6026 | 838503.8748
| 1529 | -29.1771 | 177.3763 | -29.1909 | -29.2 | 1529 | 63.7083 | 177.3763 | 838681.2512
| 1530 | -29.1909 | 177.1504 | -29.2047 | -29.2 | 1530 | 63.75 | 177.1504 | 838858.4015
| 1531 | -29.2047 | 176.9247 | -29.2184 | -29.2 | 1531 | 63.7917 | 176.9247 | 839035.3262
| 1532 | -29.2184 | 176.6993 | -29.2322 | -29.2 | 1532 | 63.8333 | 176.6993 | 839212.0255
| 1533 | -29.2322 | 176.4742 | -29.2459 | -29.2 | 1533 | 63.875 | 176.4742 | 839388.4997
| 1534 | -29.2459 | 176.2494 | -29.2596 | -29.3 | 1534 | 63.9167 | 176.2494 | 839564.7491
| 1535 | -29.2596 | 176.0249 | -29.2733 | -29.3 | 1535 | 63.9583 | 176.0249 | 839740.774
| 1536 | -29.2733 | 175.8006 | -29.2869 | -29.3 | 1536 | 64 | 175.8006 | 839916.5746
| 1537 | -29.2869 | 175.5767 | -29.3006 | -29.3 | 1537 | 64.0417 | 175.5767 | 840092.1512
| 1538 | -29.3006 | 175.353 | -29.3142 | -29.3 | 1538 | 64.0833 | 175.353 | 840267.5042
| 1539 | -29.3142 | 175.1296 | -29.3278 | -29.3 | 1539 | 64.125 | 175.1296 | 840442.6338
| 1540 | -29.3278 | 174.9065 | -29.3414 | -29.3 | 1540 | 64.1667 | 174.9065 | 840617.5403
| 1541 | -29.3414 | 174.6837 | -29.355 | -29.4 | 1541 | 64.2083 | 174.6837 | 840792.224
| 1542 | -29.355 | 174.4611 | -29.3686 | -29.4 | 1542 | 64.25 | 174.4611 | 840966.6852
| 1543 | -29.3686 | 174.2389 | -29.3821 | -29.4 | 1543 | 64.2917 | 174.2389 | 841140.9241
| 1544 | -29.3821 | 174.0169 | -29.3956 | -29.4 | 1544 | 64.3333 | 174.0169 | 841314.941
| 1545 | -29.3956 | 173.7952 | -29.4092 | -29.4 | 1545 | 64.375 | 173.7952 | 841488.7362
| 1546 | -29.4092 | 173.5738 | -29.4226 | -29.4 | 1546 | 64.4167 | 173.5738 | 841662.3101
| 1547 | -29.4226 | 173.3527 | -29.4361 | -29.4 | 1547 | 64.4583 | 173.3527 | 841835.6628
| 1548 | -29.4361 | 173.1319 | -29.4496 | -29.4 | 1548 | 64.5 | 173.1319 | 842008.7947
| 1549 | -29.4496 | 172.9113 | -29.463 | -29.5 | 1549 | 64.5417 | 172.9113 | 842181.706
| 1550 | -29.463 | 172.6911 | -29.4764 | -29.5 | 1550 | 64.5833 | 172.6911 | 842354.3971
| 1551 | -29.4764 | 172.4711 | -29.4898 | -29.5 | 1551 | 64.625 | 172.4711 | 842526.8681
| 1552 | -29.4898 | 172.2513 | -29.5032 | -29.5 | 1552 | 64.6667 | 172.2513 | 842699.1195
| 1553 | -29.5032 | 172.0319 | -29.5166 | -29.5 | 1553 | 64.7083 | 172.0319 | 842871.1514
| 1554 | -29.5166 | 171.8128 | -29.53 | -29.5 | 1554 | 64.75 | 171.8128 | 843042.9641
| 1555 | -29.53 | 171.5939 | -29.5433 | -29.5 | 1555 | 64.7917 | 171.5939 | 843214.558
| 1556 | -29.5433 | 171.3753 | -29.5566 | -29.6 | 1556 | 64.8333 | 171.3753 | 843385.9333
| 1557 | -29.5566 | 171.157 | -29.5699 | -29.6 | 1557 | 64.875 | 171.157 | 843557.0903
| 1558 | -29.5699 | 170.9389 | -29.5832 | -29.6 | 1558 | 64.9167 | 170.9389 | 843728.0292
| 1559 | -29.5832 | 170.7212 | -29.5965 | -29.6 | 1559 | 64.9583 | 170.7212 | 843898.7503
| 1560 | -29.5965 | 170.5037 | -29.6097 | -29.6 | 1560 | 65 | 170.5037 | 844069.254
| 1561 | -29.6097 | 170.2865 | -29.623 | -29.6 | 1561 | 65.0417 | 170.2865 | 844239.5405
| 1562 | -29.623 | 170.0695 | -29.6362 | -29.6 | 1562 | 65.0833 | 170.0695 | 844409.61
| 1563 | -29.6362 | 169.8529 | -29.6494 | -29.6 | 1563 | 65.125 | 169.8529 | 844579.4629
| 1564 | -29.6494 | 169.6365 | -29.6626 | -29.7 | 1564 | 65.1667 | 169.6365 | 844749.0993
| 1565 | -29.6626 | 169.4204 | -29.6757 | -29.7 | 1565 | 65.2083 | 169.4204 | 844918.5197
| 1566 | -29.6757 | 169.2046 | -29.6889 | -29.7 | 1566 | 65.25 | 169.2046 | 845087.7243
| 1567 | -29.6889 | 168.989 | -29.702 | -29.7 | 1567 | 65.2917 | 168.989 | 845256.7133
| 1568 | -29.702 | 168.7737 | -29.7152 | -29.7 | 1568 | 65.3333 | 168.7737 | 845425.487
| 1569 | -29.7152 | 168.5587 | -29.7283 | -29.7 | 1569 | 65.375 | 168.5587 | 845594.0457
| 1570 | -29.7283 | 168.344 | -29.7413 | -29.7 | 1570 | 65.4167 | 168.344 | 845762.3897
| 1571 | -29.7413 | 168.1295 | -29.7544 | -29.8 | 1571 | 65.4583 | 168.1295 | 845930.5193
| 1572 | -29.7544 | 167.9153 | -29.7675 | -29.8 | 1572 | 65.5 | 167.9153 | 846098.4346
| 1573 | -29.7675 | 167.7014 | -29.7805 | -29.8 | 1573 | 65.5417 | 167.7014 | 846266.1361
| 1574 | -29.7805 | 167.4878 | -29.7935 | -29.8 | 1574 | 65.5833 | 167.4878 | 846433.6238
| 1575 | -29.7935 | 167.2744 | -29.8065 | -29.8 | 1575 | 65.625 | 167.2744 | 846600.8983
| 1576 | -29.8065 | 167.0613 | -29.8195 | -29.8 | 1576 | 65.6667 | 167.0613 | 846767.9596
| 1577 | -29.8195 | 166.8485 | -29.8325 | -29.8 | 1577 | 65.7083 | 166.8485 | 846934.8081
| 1578 | -29.8325 | 166.636 | -29.8454 | -29.8 | 1578 | 65.75 | 166.636 | 847101.4441
| 1579 | -29.8454 | 166.4237 | -29.8584 | -29.9 | 1579 | 65.7917 | 166.4237 | 847267.8678
| 1580 | -29.8584 | 166.2117 | -29.8713 | -29.9 | 1580 | 65.8333 | 166.2117 | 847434.0794
| 1581 | -29.8713 | 165.9999 | -29.8842 | -29.9 | 1581 | 65.875 | 165.9999 | 847600.0794
| 1582 | -29.8842 | 165.7885 | -29.8971 | -29.9 | 1582 | 65.9167 | 165.7885 | 847765.8678
| 1583 | -29.8971 | 165.5773 | -29.9099 | -29.9 | 1583 | 65.9583 | 165.5773 | 847931.4451
| 1584 | -29.9099 | 165.3663 | -29.9228 | -29.9 | 1584 | 66 | 165.3663 | 848096.8114
| 1585 | -29.9228 | 165.1557 | -29.9356 | -29.9 | 1585 | 66.0417 | 165.1557 | 848261.967
| 1586 | -29.9356 | 164.9453 | -29.9485 | -29.9 | 1586 | 66.0833 | 164.9453 | 848426.9123
| 1587 | -29.9485 | 164.7351 | -29.9613 | -30 | 1587 | 66.125 | 164.7351 | 848591.6474
| 1588 | -29.9613 | 164.5253 | -29.9741 | -30 | 1588 | 66.1667 | 164.5253 | 848756.1727
| 1589 | -29.9741 | 164.3157 | -29.9868 | -30 | 1589 | 66.2083 | 164.3157 | 848920.4884
| 1590 | -29.9868 | 164.1064 | -29.9996 | -30 | 1590 | 66.25 | 164.1064 | 849084.5947
| 1591 | -29.9996 | 163.8973 | -30.0123 | -30 | 1591 | 66.2917 | 163.8973 | 849248.492
| 1592 | -30.0123 | 163.6885 | -30.025 | -30 | 1592 | 66.3333 | 163.6885 | 849412.1805
| 1593 | -30.025 | 163.48 | -30.0378 | -30 | 1593 | 66.375 | 163.48 | 849575.6605
| 1594 | -30.0378 | 163.2717 | -30.0504 | -30.1 | 1594 | 66.4167 | 163.2717 | 849738.9322
| 1595 | -30.0504 | 163.0637 | -30.0631 | -30.1 | 1595 | 66.4583 | 163.0637 | 849901.9959
| 1596 | -30.0631 | 162.856 | -30.0758 | -30.1 | 1596 | 66.5 | 162.856 | 850064.8519
| 1597 | -30.0758 | 162.6485 | -30.0884 | -30.1 | 1597 | 66.5417 | 162.6485 | 850227.5004
| 1598 | -30.0884 | 162.4413 | -30.101 | -30.1 | 1598 | 66.5833 | 162.4413 | 850389.9417
| 1599 | -30.101 | 162.2344 | -30.1137 | -30.1 | 1599 | 66.625 | 162.2344 | 850552.1761
| 1600 | -30.1137 | 162.0277 | -30.1262 | -30.1 | 1600 | 66.6667 | 162.0277 | 850714.2038
| 1601 | -30.1262 | 161.8213 | -30.1388 | -30.1 | 1601 | 66.7083 | 161.8213 | 850876.0251
| 1602 | -30.1388 | 161.6151 | -30.1514 | -30.2 | 1602 | 66.75 | 161.6151 | 851037.6403
| 1603 | -30.1514 | 161.4093 | -30.1639 | -30.2 | 1603 | 66.7917 | 161.4093 | 851199.0495
| 1604 | -30.1639 | 161.2036 | -30.1765 | -30.2 | 1604 | 66.8333 | 161.2036 | 851360.2532
| 1605 | -30.1765 | 160.9983 | -30.189 | -30.2 | 1605 | 66.875 | 160.9983 | 851521.2514
| 1606 | -30.189 | 160.7932 | -30.2015 | -30.2 | 1606 | 66.9167 | 160.7932 | 851682.0446
| 1607 | -30.2015 | 160.5883 | -30.214 | -30.2 | 1607 | 66.9583 | 160.5883 | 851842.633
| 1608 | -30.214 | 160.3838 | -30.2264 | -30.2 | 1608 | 67 | 160.3838 | 852003.0167
| 1609 | -30.2264 | 160.1794 | -30.2389 | -30.2 | 1609 | 67.0417 | 160.1794 | 852163.1962
| 1610 | -30.2389 | 159.9754 | -30.2513 | -30.3 | 1610 | 67.0833 | 159.9754 | 852323.1715
| 1611 | -30.2513 | 159.7716 | -30.2637 | -30.3 | 1611 | 67.125 | 159.7716 | 852482.9431
| 1612 | -30.2637 | 159.5681 | -30.2761 | -30.3 | 1612 | 67.1667 | 159.5681 | 852642.5112
| 1613 | -30.2761 | 159.3648 | -30.2885 | -30.3 | 1613 | 67.2083 | 159.3648 | 852801.876
| 1614 | -30.2885 | 159.1618 | -30.3009 | -30.3 | 1614 | 67.25 | 159.1618 | 852961.0377
| 1615 | -30.3009 | 158.959 | -30.3133 | -30.3 | 1615 | 67.2917 | 158.959 | 853119.9967
| 1616 | -30.3133 | 158.7565 | -30.3256 | -30.3 | 1616 | 67.3333 | 158.7565 | 853278.7532
| 1617 | -30.3256 | 158.5543 | -30.3379 | -30.3 | 1617 | 67.375 | 158.5543 | 853437.3075
| 1618 | -30.3379 | 158.3523 | -30.3502 | -30.4 | 1618 | 67.4167 | 158.3523 | 853595.6597
| 1619 | -30.3502 | 158.1505 | -30.3625 | -30.4 | 1619 | 67.4583 | 158.1505 | 853753.8103
| 1620 | -30.3625 | 157.9491 | -30.3748 | -30.4 | 1620 | 67.5 | 157.9491 | 853911.7593
| 1621 | -30.3748 | 157.7478 | -30.3871 | -30.4 | 1621 | 67.5417 | 157.7478 | 854069.5072
| 1622 | -30.3871 | 157.5469 | -30.3993 | -30.4 | 1622 | 67.5833 | 157.5469 | 854227.0541
| 1623 | -30.3993 | 157.3462 | -30.4115 | -30.4 | 1623 | 67.625 | 157.3462 | 854384.4003
| 1624 | -30.4115 | 157.1457 | -30.4238 | -30.4 | 1624 | 67.6667 | 157.1457 | 854541.546
| 1625 | -30.4238 | 156.9455 | -30.4359 | -30.4 | 1625 | 67.7083 | 156.9455 | 854698.4915
| 1626 | -30.4359 | 156.7456 | -30.4481 | -30.4 | 1626 | 67.75 | 156.7456 | 854855.2372
| 1627 | -30.4481 | 156.5459 | -30.4603 | -30.5 | 1627 | 67.7917 | 156.5459 | 855011.7831
| 1628 | -30.4603 | 156.3465 | -30.4725 | -30.5 | 1628 | 67.8333 | 156.3465 | 855168.1296
| 1629 | -30.4725 | 156.1473 | -30.4846 | -30.5 | 1629 | 67.875 | 156.1473 | 855324.2769
| 1630 | -30.4846 | 155.9484 | -30.4967 | -30.5 | 1630 | 67.9167 | 155.9484 | 855480.2253
| 1631 | -30.4967 | 155.7497 | -30.5088 | -30.5 | 1631 | 67.9583 | 155.7497 | 855635.9751
| 1632 | -30.5088 | 155.5513 | -30.5209 | -30.5 | 1632 | 68 | 155.5513 | 855791.5264
| 1633 | -30.5209 | 155.3532 | -30.533 | -30.5 | 1633 | 68.0417 | 155.3532 | 855946.8796
| 1634 | -30.533 | 155.1553 | -30.545 | -30.5 | 1634 | 68.0833 | 155.1553 | 856102.0348
| 1635 | -30.545 | 154.9576 | -30.5571 | -30.6 | 1635 | 68.125 | 154.9576 | 856256.9924
| 1636 | -30.5571 | 154.7602 | -30.5691 | -30.6 | 1636 | 68.1667 | 154.7602 | 856411.7526
| 1637 | -30.5691 | 154.563 | -30.5811 | -30.6 | 1637 | 68.2083 | 154.563 | 856566.3157
| 1638 | -30.5811 | 154.3661 | -30.5931 | -30.6 | 1638 | 68.25 | 154.3661 | 856720.6818
| 1639 | -30.5931 | 154.1695 | -30.6051 | -30.6 | 1639 | 68.2917 | 154.1695 | 856874.8513
| 1640 | -30.6051 | 153.9731 | -30.6171 | -30.6 | 1640 | 68.3333 | 153.9731 | 857028.8244
| 1641 | -30.6171 | 153.7769 | -30.629 | -30.6 | 1641 | 68.375 | 153.7769 | 857182.6013
| 1642 | -30.629 | 153.581 | -30.641 | -30.6 | 1642 | 68.4167 | 153.581 | 857336.1824
| 1643 | -30.641 | 153.3854 | -30.6529 | -30.7 | 1643 | 68.4583 | 153.3854 | 857489.5678
| 1644 | -30.6529 | 153.19 | -30.6648 | -30.7 | 1644 | 68.5 | 153.19 | 857642.7578
| 1645 | -30.6648 | 152.9948 | -30.6767 | -30.7 | 1645 | 68.5417 | 152.9948 | 857795.7526
| 1646 | -30.6767 | 152.7999 | -30.6886 | -30.7 | 1646 | 68.5833 | 152.7999 | 857948.5525
| 1647 | -30.6886 | 152.6053 | -30.7004 | -30.7 | 1647 | 68.625 | 152.6053 | 858101.1578
| 1648 | -30.7004 | 152.4109 | -30.7123 | -30.7 | 1648 | 68.6667 | 152.4109 | 858253.5687
| 1649 | -30.7123 | 152.2167 | -30.7241 | -30.7 | 1649 | 68.7083 | 152.2167 | 858405.7854
| 1650 | -30.7241 | 152.0228 | -30.7359 | -30.7 | 1650 | 68.75 | 152.0228 | 858557.8082
| 1651 | -30.7359 | 151.8291 | -30.7477 | -30.7 | 1651 | 68.7917 | 151.8291 | 858709.6373
| 1652 | -30.7477 | 151.6357 | -30.7595 | -30.8 | 1652 | 68.8333 | 151.6357 | 858861.273
| 1653 | -30.7595 | 151.4425 | -30.7713 | -30.8 | 1653 | 68.875 | 151.4425 | 859012.7156
| 1654 | -30.7713 | 151.2496 | -30.7831 | -30.8 | 1654 | 68.9167 | 151.2496 | 859163.9652
| 1655 | -30.7831 | 151.0569 | -30.7948 | -30.8 | 1655 | 68.9583 | 151.0569 | 859315.0221
| 1656 | -30.7948 | 150.8645 | -30.8065 | -30.8 | 1656 | 69 | 150.8645 | 859465.8866
| 1657 | -30.8065 | 150.6723 | -30.8182 | -30.8 | 1657 | 69.0417 | 150.6723 | 859616.5589
| 1658 | -30.8182 | 150.4804 | -30.8299 | -30.8 | 1658 | 69.0833 | 150.4804 | 859767.0393
| 1659 | -30.8299 | 150.2887 | -30.8416 | -30.8 | 1659 | 69.125 | 150.2887 | 859917.328
| 1660 | -30.8416 | 150.0972 | -30.8533 | -30.9 | 1660 | 69.1667 | 150.0972 | 860067.4252
| 1661 | -30.8533 | 149.906 | -30.8649 | -30.9 | 1661 | 69.2083 | 149.906 | 860217.3312
| 1662 | -30.8649 | 149.715 | -30.8766 | -30.9 | 1662 | 69.25 | 149.715 | 860367.0462
| 1663 | -30.8766 | 149.5243 | -30.8882 | -30.9 | 1663 | 69.2917 | 149.5243 | 860516.5705
| 1664 | -30.8882 | 149.3338 | -30.8998 | -30.9 | 1664 | 69.3333 | 149.3338 | 860665.9043
| 1665 | -30.8998 | 149.1436 | -30.9114 | -30.9 | 1665 | 69.375 | 149.1436 | 860815.0479
| 1666 | -30.9114 | 148.9536 | -30.923 | -30.9 | 1666 | 69.4167 | 148.9536 | 860964.0015
| 1667 | -30.923 | 148.7638 | -30.9345 | -30.9 | 1667 | 69.4583 | 148.7638 | 861112.7653
| 1668 | -30.9345 | 148.5743 | -30.9461 | -30.9 | 1668 | 69.5 | 148.5743 | 861261.3396
| 1669 | -30.9461 | 148.385 | -30.9576 | -31 | 1669 | 69.5417 | 148.385 | 861409.7247
| 1670 | -30.9576 | 148.196 | -30.9691 | -31 | 1670 | 69.5833 | 148.196 | 861557.9207
| 1671 | -30.9691 | 148.0072 | -30.9806 | -31 | 1671 | 69.625 | 148.0072 | 861705.9279
| 1672 | -30.9806 | 147.8187 | -30.9921 | -31 | 1672 | 69.6667 | 147.8187 | 861853.7465
| 1673 | -30.9921 | 147.6304 | -31.0036 | -31 | 1673 | 69.7083 | 147.6304 | 862001.3769
| 1674 | -31.0036 | 147.4423 | -31.0151 | -31 | 1674 | 69.75 | 147.4423 | 862148.8192
| 1675 | -31.0151 | 147.2545 | -31.0265 | -31 | 1675 | 69.7917 | 147.2545 | 862296.0736
| 1676 | -31.0265 | 147.0669 | -31.0379 | -31 | 1676 | 69.8333 | 147.0669 | 862443.1405
| 1677 | -31.0379 | 146.8795 | -31.0494 | -31 | 1677 | 69.875 | 146.8795 | 862590.02
| 1678 | -31.0494 | 146.6924 | -31.0608 | -31.1 | 1678 | 69.9167 | 146.6924 | 862736.7124
| 1679 | -31.0608 | 146.5055 | -31.0722 | -31.1 | 1679 | 69.9583 | 146.5055 | 862883.2179
| 1680 | -31.0722 | 146.3189 | -31.0835 | -31.1 | 1680 | 70 | 146.3189 | 863029.5368
| 1681 | -31.0835 | 146.1325 | -31.0949 | -31.1 | 1681 | 70.0417 | 146.1325 | 863175.6693
| 1682 | -31.0949 | 145.9463 | -31.1062 | -31.1 | 1682 | 70.0833 | 145.9463 | 863321.6156
| 1683 | -31.1062 | 145.7604 | -31.1176 | -31.1 | 1683 | 70.125 | 145.7604 | 863467.376
| 1684 | -31.1176 | 145.5747 | -31.1289 | -31.1 | 1684 | 70.1667 | 145.5747 | 863612.9508
| 1685 | -31.1289 | 145.3893 | -31.1402 | -31.1 | 1685 | 70.2083 | 145.3893 | 863758.34
| 1686 | -31.1402 | 145.204 | -31.1515 | -31.2 | 1686 | 70.25 | 145.204 | 863903.5441
| 1687 | -31.1515 | 145.0191 | -31.1627 | -31.2 | 1687 | 70.2917 | 145.0191 | 864048.5631
| 1688 | -31.1627 | 144.8343 | -31.174 | -31.2 | 1688 | 70.3333 | 144.8343 | 864193.3975
| 1689 | -31.174 | 144.6498 | -31.1852 | -31.2 | 1689 | 70.375 | 144.6498 | 864338.0473
| 1690 | -31.1852 | 144.4655 | -31.1965 | -31.2 | 1690 | 70.4167 | 144.4655 | 864482.5128
| 1691 | -31.1965 | 144.2815 | -31.2077 | -31.2 | 1691 | 70.4583 | 144.2815 | 864626.7943
| 1692 | -31.2077 | 144.0977 | -31.2189 | -31.2 | 1692 | 70.5 | 144.0977 | 864770.892
| 1693 | -31.2189 | 143.9141 | -31.2301 | -31.2 | 1693 | 70.5417 | 143.9141 | 864914.8062
| 1694 | -31.2301 | 143.7308 | -31.2412 | -31.2 | 1694 | 70.5833 | 143.7308 | 865058.5369
| 1695 | -31.2412 | 143.5477 | -31.2524 | -31.3 | 1695 | 70.625 | 143.5477 | 865202.0846
| 1696 | -31.2524 | 143.3648 | -31.2635 | -31.3 | 1696 | 70.6667 | 143.3648 | 865345.4495
| 1697 | -31.2635 | 143.1822 | -31.2747 | -31.3 | 1697 | 70.7083 | 143.1822 | 865488.6317
| 1698 | -31.2747 | 142.9998 | -31.2858 | -31.3 | 1698 | 70.75 | 142.9998 | 865631.6314
| 1699 | -31.2858 | 142.8176 | -31.2969 | -31.3 | 1699 | 70.7917 | 142.8176 | 865774.4491
| 1700 | -31.2969 | 142.6357 | -31.308 | -31.3 | 1700 | 70.8333 | 142.6357 | 865917.0847
| 1701 | -31.308 | 142.454 | -31.319 | -31.3 | 1701 | 70.875 | 142.454 | 866059.5387
| 1702 | -31.319 | 142.2725 | -31.3301 | -31.3 | 1702 | 70.9167 | 142.2725 | 866201.8112
| 1703 | -31.3301 | 142.0912 | -31.3412 | -31.3 | 1703 | 70.9583 | 142.0912 | 866343.9024
| 1704 | -31.3412 | 141.9102 | -31.3522 | -31.4 | 1704 | 71 | 141.9102 | 866485.8127
| 1705 | -31.3522 | 141.7295 | -31.3632 | -31.4 | 1705 | 71.0417 | 141.7295 | 866627.5421
| 1706 | -31.3632 | 141.5489 | -31.3742 | -31.4 | 1706 | 71.0833 | 141.5489 | 866769.091
| 1707 | -31.3742 | 141.3686 | -31.3852 | -31.4 | 1707 | 71.125 | 141.3686 | 866910.4596
| 1708 | -31.3852 | 141.1885 | -31.3962 | -31.4 | 1708 | 71.1667 | 141.1885 | 867051.6481
| 1709 | -31.3962 | 141.0086 | -31.4071 | -31.4 | 1709 | 71.2083 | 141.0086 | 867192.6567
| 1710 | -31.4071 | 140.829 | -31.4181 | -31.4 | 1710 | 71.25 | 140.829 | 867333.4857
| 1711 | -31.4181 | 140.6496 | -31.429 | -31.4 | 1711 | 71.2917 | 140.6496 | 867474.1353
| 1712 | -31.429 | 140.4704 | -31.4399 | -31.4 | 1712 | 71.3333 | 140.4704 | 867614.6057
| 1713 | -31.4399 | 140.2915 | -31.4508 | -31.5 | 1713 | 71.375 | 140.2915 | 867754.8971
| 1714 | -31.4508 | 140.1127 | -31.4617 | -31.5 | 1714 | 71.4167 | 140.1127 | 867895.0099
| 1715 | -31.4617 | 139.9342 | -31.4726 | -31.5 | 1715 | 71.4583 | 139.9342 | 868034.9441
| 1716 | -31.4726 | 139.756 | -31.4835 | -31.5 | 1716 | 71.5 | 139.756 | 868174.7001
| 1717 | -31.4835 | 139.5779 | -31.4943 | -31.5 | 1717 | 71.5417 | 139.5779 | 868314.278
| 1718 | -31.4943 | 139.4001 | -31.5051 | -31.5 | 1718 | 71.5833 | 139.4001 | 868453.6782
| 1719 | -31.5051 | 139.2225 | -31.516 | -31.5 | 1719 | 71.625 | 139.2225 | 868592.9007
| 1720 | -31.516 | 139.0452 | -31.5268 | -31.5 | 1720 | 71.6667 | 139.0452 | 868731.9459
| 1721 | -31.5268 | 138.868 | -31.5376 | -31.5 | 1721 | 71.7083 | 138.868 | 868870.8139
| 1722 | -31.5376 | 138.6911 | -31.5483 | -31.5 | 1722 | 71.75 | 138.6911 | 869009.5051
| 1723 | -31.5483 | 138.5145 | -31.5591 | -31.6 | 1723 | 71.7917 | 138.5145 | 869148.0195
| 1724 | -31.5591 | 138.338 | -31.5699 | -31.6 | 1724 | 71.8333 | 138.338 | 869286.3575
| 1725 | -31.5699 | 138.1618 | -31.5806 | -31.6 | 1725 | 71.875 | 138.1618 | 869424.5193
| 1726 | -31.5806 | 137.9858 | -31.5913 | -31.6 | 1726 | 71.9167 | 137.9858 | 869562.5051
| 1727 | -31.5913 | 137.81 | -31.602 | -31.6 | 1727 | 71.9583 | 137.81 | 869700.315
| 1728 | -31.602 | 137.6344 | -31.6127 | -31.6 | 1728 | 72 | 137.6344 | 869837.9495
| 1729 | -31.6127 | 137.4591 | -31.6234 | -31.6 | 1729 | 72.0417 | 137.4591 | 869975.4085
| 1730 | -31.6234 | 137.284 | -31.6341 | -31.6 | 1730 | 72.0833 | 137.284 | 870112.6925
| 1731 | -31.6341 | 137.1091 | -31.6448 | -31.6 | 1731 | 72.125 | 137.1091 | 870249.8016
| 1732 | -31.6448 | 136.9344 | -31.6554 | -31.7 | 1732 | 72.1667 | 136.9344 | 870386.736
| 1733 | -31.6554 | 136.76 | -31.666 | -31.7 | 1733 | 72.2083 | 136.76 | 870523.496
| 1734 | -31.666 | 136.5857 | -31.6766 | -31.7 | 1734 | 72.25 | 136.5857 | 870660.0817
| 1735 | -31.6766 | 136.4117 | -31.6873 | -31.7 | 1735 | 72.2917 | 136.4117 | 870796.4935
| 1736 | -31.6873 | 136.238 | -31.6978 | -31.7 | 1736 | 72.3333 | 136.238 | 870932.7314
| 1737 | -31.6978 | 136.0644 | -31.7084 | -31.7 | 1737 | 72.375 | 136.0644 | 871068.7959
| 1738 | -31.7084 | 135.8911 | -31.719 | -31.7 | 1738 | 72.4167 | 135.8911 | 871204.6869
| 1739 | -31.719 | 135.718 | -31.7295 | -31.7 | 1739 | 72.4583 | 135.718 | 871340.4049
| 1740 | -31.7295 | 135.5451 | -31.7401 | -31.7 | 1740 | 72.5 | 135.5451 | 871475.95
| 1741 | -31.7401 | 135.3724 | -31.7506 | -31.8 | 1741 | 72.5417 | 135.3724 | 871611.3224
| 1742 | -31.7506 | 135.1999 | -31.7611 | -31.8 | 1742 | 72.5833 | 135.1999 | 871746.5223
| 1743 | -31.7611 | 135.0277 | -31.7716 | -31.8 | 1743 | 72.625 | 135.0277 | 871881.55
| 1744 | -31.7716 | 134.8557 | -31.7821 | -31.8 | 1744 | 72.6667 | 134.8557 | 872016.4057
| 1745 | -31.7821 | 134.6839 | -31.7925 | -31.8 | 1745 | 72.7083 | 134.6839 | 872151.0896
| 1746 | -31.7925 | 134.5123 | -31.803 | -31.8 | 1746 | 72.75 | 134.5123 | 872285.6019
| 1747 | -31.803 | 134.341 | -31.8134 | -31.8 | 1747 | 72.7917 | 134.341 | 872419.9429
| 1748 | -31.8134 | 134.1698 | -31.8239 | -31.8 | 1748 | 72.8333 | 134.1698 | 872554.1127
| 1749 | -31.8239 | 133.9989 | -31.8343 | -31.8 | 1749 | 72.875 | 133.9989 | 872688.1116
| 1750 | -31.8343 | 133.8282 | -31.8447 | -31.8 | 1750 | 72.9167 | 133.8282 | 872821.9398
| 1751 | -31.8447 | 133.6577 | -31.8551 | -31.9 | 1751 | 72.9583 | 133.6577 | 872955.5975
| 1752 | -31.8551 | 133.4874 | -31.8655 | -31.9 | 1752 | 73 | 133.4874 | 873089.0849
| 1753 | -31.8655 | 133.3174 | -31.8758 | -31.9 | 1753 | 73.0417 | 133.3174 | 873222.4023
| 1754 | -31.8758 | 133.1475 | -31.8862 | -31.9 | 1754 | 73.0833 | 133.1475 | 873355.5498
| 1755 | -31.8862 | 132.9779 | -31.8965 | -31.9 | 1755 | 73.125 | 132.9779 | 873488.5278
| 1756 | -31.8965 | 132.8085 | -31.9068 | -31.9 | 1756 | 73.1667 | 132.8085 | 873621.3363
| 1757 | -31.9068 | 132.6393 | -31.9171 | -31.9 | 1757 | 73.2083 | 132.6393 | 873753.9756
| 1758 | -31.9171 | 132.4704 | -31.9274 | -31.9 | 1758 | 73.25 | 132.4704 | 873886.446
| 1759 | -31.9274 | 132.3016 | -31.9377 | -31.9 | 1759 | 73.2917 | 132.3016 | 874018.7476
| 1760 | -31.9377 | 132.1331 | -31.948 | -31.9 | 1760 | 73.3333 | 132.1331 | 874150.8806
| 1761 | -31.948 | 131.9647 | -31.9582 | -32 | 1761 | 73.375 | 131.9647 | 874282.8454
| 1762 | -31.9582 | 131.7966 | -31.9685 | -32 | 1762 | 73.4167 | 131.7966 | 874414.642
| 1763 | -31.9685 | 131.6287 | -31.9787 | -32 | 1763 | 73.4583 | 131.6287 | 874546.2707
| 1764 | -31.9787 | 131.461 | -31.9889 | -32 | 1764 | 73.5 | 131.461 | 874677.7317
| 1765 | -31.9889 | 131.2936 | -31.9991 | -32 | 1765 | 73.5417 | 131.2936 | 874809.0253
| 1766 | -31.9991 | 131.1263 | -32.0093 | -32 | 1766 | 73.5833 | 131.1263 | 874940.1516
| 1767 | -32.0093 | 130.9593 | -32.0195 | -32 | 1767 | 73.625 | 130.9593 | 875071.1109
| 1768 | -32.0195 | 130.7924 | -32.0297 | -32 | 1768 | 73.6667 | 130.7924 | 875201.9033
| 1769 | -32.0297 | 130.6258 | -32.0398 | -32 | 1769 | 73.7083 | 130.6258 | 875332.5291
| 1770 | -32.0398 | 130.4594 | -32.05 | -32 | 1770 | 73.75 | 130.4594 | 875462.9885
| 1771 | -32.05 | 130.2932 | -32.0601 | -32.1 | 1771 | 73.7917 | 130.2932 | 875593.2817
| 1772 | -32.0601 | 130.1272 | -32.0702 | -32.1 | 1772 | 73.8333 | 130.1272 | 875723.4089
| 1773 | -32.0702 | 129.9615 | -32.0803 | -32.1 | 1773 | 73.875 | 129.9615 | 875853.3704
| 1774 | -32.0803 | 129.7959 | -32.0904 | -32.1 | 1774 | 73.9167 | 129.7959 | 875983.1663
| 1775 | -32.0904 | 129.6305 | -32.1005 | -32.1 | 1775 | 73.9583 | 129.6305 | 876112.7968
| 1776 | -32.1005 | 129.4654 | -32.1106 | -32.1 | 1776 | 74 | 129.4654 | 876242.2622
| 1777 | -32.1106 | 129.3005 | -32.1206 | -32.1 | 1777 | 74.0417 | 129.3005 | 876371.5627
| 1778 | -32.1206 | 129.1358 | -32.1306 | -32.1 | 1778 | 74.0833 | 129.1358 | 876500.6985
| 1779 | -32.1306 | 128.9712 | -32.1407 | -32.1 | 1779 | 74.125 | 128.9712 | 876629.6697
| 1780 | -32.1407 | 128.8069 | -32.1507 | -32.2 | 1780 | 74.1667 | 128.8069 | 876758.4766
| 1781 | -32.1507 | 128.6429 | -32.1607 | -32.2 | 1781 | 74.2083 | 128.6429 | 876887.1195
| 1782 | -32.1607 | 128.479 | -32.1707 | -32.2 | 1782 | 74.25 | 128.479 | 877015.5985
| 1783 | -32.1707 | 128.3153 | -32.1806 | -32.2 | 1783 | 74.2917 | 128.3153 | 877143.9138
| 1784 | -32.1806 | 128.1518 | -32.1906 | -32.2 | 1784 | 74.3333 | 128.1518 | 877272.0656
| 1785 | -32.1906 | 127.9886 | -32.2005 | -32.2 | 1785 | 74.375 | 127.9886 | 877400.0542
| 1786 | -32.2005 | 127.8255 | -32.2105 | -32.2 | 1786 | 74.4167 | 127.8255 | 877527.8797
| 1787 | -32.2105 | 127.6627 | -32.2204 | -32.2 | 1787 | 74.4583 | 127.6627 | 877655.5424
| 1788 | -32.2204 | 127.5001 | -32.2303 | -32.2 | 1788 | 74.5 | 127.5001 | 877783.0425
| 1789 | -32.2303 | 127.3376 | -32.2402 | -32.2 | 1789 | 74.5417 | 127.3376 | 877910.3801
| 1790 | -32.2402 | 127.1754 | -32.2501 | -32.3 | 1790 | 74.5833 | 127.1754 | 878037.5555
| 1791 | -32.2501 | 127.0134 | -32.26 | -32.3 | 1791 | 74.625 | 127.0134 | 878164.5689
| 1792 | -32.26 | 126.8516 | -32.2698 | -32.3 | 1792 | 74.6667 | 126.8516 | 878291.4205
| 1793 | -32.2698 | 126.69 | -32.2797 | -32.3 | 1793 | 74.7083 | 126.69 | 878418.1105
| 1794 | -32.2797 | 126.5286 | -32.2895 | -32.3 | 1794 | 74.75 | 126.5286 | 878544.6391
| 1795 | -32.2895 | 126.3674 | -32.2993 | -32.3 | 1795 | 74.7917 | 126.3674 | 878671.0065
| 1796 | -32.2993 | 126.2064 | -32.3091 | -32.3 | 1796 | 74.8333 | 126.2064 | 878797.213
| 1797 | -32.3091 | 126.0457 | -32.3189 | -32.3 | 1797 | 74.875 | 126.0457 | 878923.2586
| 1798 | -32.3189 | 125.8851 | -32.3287 | -32.3 | 1798 | 74.9167 | 125.8851 | 879049.1437
| 1799 | -32.3287 | 125.7247 | -32.3385 | -32.3 | 1799 | 74.9583 | 125.7247 | 879174.8684
| 1800 | -32.3385 | 125.5646 | -32.3483 | -32.3 | 1800 | 75 | 125.5646 | 879300.433
| 1801 | -32.3483 | 125.4046 | -32.358 | -32.4 | 1801 | 75.0417 | 125.4046 | 879425.8376
| 1802 | -32.358 | 125.2448 | -32.3677 | -32.4 | 1802 | 75.0833 | 125.2448 | 879551.0824
| 1803 | -32.3677 | 125.0853 | -32.3775 | -32.4 | 1803 | 75.125 | 125.0853 | 879676.1677
| 1804 | -32.3775 | 124.9259 | -32.3872 | -32.4 | 1804 | 75.1667 | 124.9259 | 879801.0936
| 1805 | -32.3872 | 124.7668 | -32.3969 | -32.4 | 1805 | 75.2083 | 124.7668 | 879925.8604
| 1806 | -32.3969 | 124.6078 | -32.4066 | -32.4 | 1806 | 75.25 | 124.6078 | 880050.4682
| 1807 | -32.4066 | 124.4491 | -32.4162 | -32.4 | 1807 | 75.2917 | 124.4491 | 880174.9173
| 1808 | -32.4162 | 124.2906 | -32.4259 | -32.4 | 1808 | 75.3333 | 124.2906 | 880299.2079
| 1809 | -32.4259 | 124.1322 | -32.4355 | -32.4 | 1809 | 75.375 | 124.1322 | 880423.3401
| 1810 | -32.4355 | 123.9741 | -32.4452 | -32.4 | 1810 | 75.4167 | 123.9741 | 880547.3142
| 1811 | -32.4452 | 123.8162 | -32.4548 | -32.5 | 1811 | 75.4583 | 123.8162 | 880671.1304
| 1812 | -32.4548 | 123.6584 | -32.4644 | -32.5 | 1812 | 75.5 | 123.6584 | 880794.7888
| 1813 | -32.4644 | 123.5009 | -32.474 | -32.5 | 1813 | 75.5417 | 123.5009 | 880918.2897
| 1814 | -32.474 | 123.3436 | -32.4836 | -32.5 | 1814 | 75.5833 | 123.3436 | 881041.6333
| 1815 | -32.4836 | 123.1864 | -32.4932 | -32.5 | 1815 | 75.625 | 123.1864 | 881164.8197
| 1816 | -32.4932 | 123.0295 | -32.5027 | -32.5 | 1816 | 75.6667 | 123.0295 | 881287.8492
| 1817 | -32.5027 | 122.8728 | -32.5123 | -32.5 | 1817 | 75.7083 | 122.8728 | 881410.722
| 1818 | -32.5123 | 122.7162 | -32.5218 | -32.5 | 1818 | 75.75 | 122.7162 | 881533.4382
| 1819 | -32.5218 | 122.5599 | -32.5314 | -32.5 | 1819 | 75.7917 | 122.5599 | 881655.9981
| 1820 | -32.5314 | 122.4038 | -32.5409 | -32.5 | 1820 | 75.8333 | 122.4038 | 881778.4019
| 1821 | -32.5409 | 122.2478 | -32.5504 | -32.6 | 1821 | 75.875 | 122.2478 | 881900.6498
| 1822 | -32.5504 | 122.0921 | -32.5599 | -32.6 | 1822 | 75.9167 | 122.0921 | 882022.7419
| 1823 | -32.5599 | 121.9366 | -32.5693 | -32.6 | 1823 | 75.9583 | 121.9366 | 882144.6784
| 1824 | -32.5693 | 121.7812 | -32.5788 | -32.6 | 1824 | 76 | 121.7812 | 882266.4597
| 1825 | -32.5788 | 121.6261 | -32.5883 | -32.6 | 1825 | 76.0417 | 121.6261 | 882388.0858
| 1826 | -32.5883 | 121.4712 | -32.5977 | -32.6 | 1826 | 76.0833 | 121.4712 | 882509.5569
| 1827 | -32.5977 | 121.3164 | -32.6071 | -32.6 | 1827 | 76.125 | 121.3164 | 882630.8733
| 1828 | -32.6071 | 121.1619 | -32.6166 | -32.6 | 1828 | 76.1667 | 121.1619 | 882752.0352
| 1829 | -32.6166 | 121.0075 | -32.626 | -32.6 | 1829 | 76.2083 | 121.0075 | 882873.0427
| 1830 | -32.626 | 120.8534 | -32.6354 | -32.6 | 1830 | 76.25 | 120.8534 | 882993.8961
| 1831 | -32.6354 | 120.6994 | -32.6447 | -32.6 | 1831 | 76.2917 | 120.6994 | 883114.5955
| 1832 | -32.6447 | 120.5456 | -32.6541 | -32.7 | 1832 | 76.3333 | 120.5456 | 883235.1411
| 1833 | -32.6541 | 120.3921 | -32.6635 | -32.7 | 1833 | 76.375 | 120.3921 | 883355.5332
| 1834 | -32.6635 | 120.2387 | -32.6728 | -32.7 | 1834 | 76.4167 | 120.2387 | 883475.7719
| 1835 | -32.6728 | 120.0855 | -32.6821 | -32.7 | 1835 | 76.4583 | 120.0855 | 883595.8574
| 1836 | -32.6821 | 119.9325 | -32.6915 | -32.7 | 1836 | 76.5 | 119.9325 | 883715.7899
| 1837 | -32.6915 | 119.7798 | -32.7008 | -32.7 | 1837 | 76.5417 | 119.7798 | 883835.5697
| 1838 | -32.7008 | 119.6272 | -32.7101 | -32.7 | 1838 | 76.5833 | 119.6272 | 883955.1969
| 1839 | -32.7101 | 119.4748 | -32.7194 | -32.7 | 1839 | 76.625 | 119.4748 | 884074.6716
| 1840 | -32.7194 | 119.3226 | -32.7286 | -32.7 | 1840 | 76.6667 | 119.3226 | 884193.9942
| 1841 | -32.7286 | 119.1706 | -32.7379 | -32.7 | 1841 | 76.7083 | 119.1706 | 884313.1648
| 1842 | -32.7379 | 119.0187 | -32.7472 | -32.7 | 1842 | 76.75 | 119.0187 | 884432.1835
| 1843 | -32.7472 | 118.8671 | -32.7564 | -32.8 | 1843 | 76.7917 | 118.8671 | 884551.0507
| 1844 | -32.7564 | 118.7157 | -32.7656 | -32.8 | 1844 | 76.8333 | 118.7157 | 884669.7664
| 1845 | -32.7656 | 118.5645 | -32.7748 | -32.8 | 1845 | 76.875 | 118.5645 | 884788.3308
| 1846 | -32.7748 | 118.4134 | -32.784 | -32.8 | 1846 | 76.9167 | 118.4134 | 884906.7443
| 1847 | -32.784 | 118.2626 | -32.7932 | -32.8 | 1847 | 76.9583 | 118.2626 | 885025.0068
| 1848 | -32.7932 | 118.1119 | -32.8024 | -32.8 | 1848 | 77 | 118.1119 | 885143.1187
| 1849 | -32.8024 | 117.9615 | -32.8116 | -32.8 | 1849 | 77.0417 | 117.9615 | 885261.0802
| 1850 | -32.8116 | 117.8112 | -32.8207 | -32.8 | 1850 | 77.0833 | 117.8112 | 885378.8914
| 1851 | -32.8207 | 117.6611 | -32.8299 | -32.8 | 1851 | 77.125 | 117.6611 | 885496.5525
| 1852 | -32.8299 | 117.5112 | -32.839 | -32.8 | 1852 | 77.1667 | 117.5112 | 885614.0637
| 1853 | -32.839 | 117.3615 | -32.8481 | -32.8 | 1853 | 77.2083 | 117.3615 | 885731.4252
| 1854 | -32.8481 | 117.212 | -32.8573 | -32.9 | 1854 | 77.25 | 117.212 | 885848.6372
| 1855 | -32.8573 | 117.0627 | -32.8664 | -32.9 | 1855 | 77.2917 | 117.0627 | 885965.6998
| 1856 | -32.8664 | 116.9135 | -32.8754 | -32.9 | 1856 | 77.3333 | 116.9135 | 886082.6134
| 1857 | -32.8754 | 116.7646 | -32.8845 | -32.9 | 1857 | 77.375 | 116.7646 | 886199.378
| 1858 | -32.8845 | 116.6159 | -32.8936 | -32.9 | 1858 | 77.4167 | 116.6159 | 886315.9938
| 1859 | -32.8936 | 116.4673 | -32.9026 | -32.9 | 1859 | 77.4583 | 116.4673 | 886432.4611
| 1860 | -32.9026 | 116.3189 | -32.9117 | -32.9 | 1860 | 77.5 | 116.3189 | 886548.7801
| 1861 | -32.9117 | 116.1707 | -32.9207 | -32.9 | 1861 | 77.5417 | 116.1707 | 886664.9508
| 1862 | -32.9207 | 116.0228 | -32.9297 | -32.9 | 1862 | 77.5833 | 116.0228 | 886780.9735
| 1863 | -32.9297 | 115.8749 | -32.9387 | -32.9 | 1863 | 77.625 | 115.8749 | 886896.8485
| 1864 | -32.9387 | 115.7273 | -32.9477 | -32.9 | 1864 | 77.6667 | 115.7273 | 887012.5758
| 1865 | -32.9477 | 115.5799 | -32.9567 | -33 | 1865 | 77.7083 | 115.5799 | 887128.1557
| 1866 | -32.9567 | 115.4327 | -32.9657 | -33 | 1866 | 77.75 | 115.4327 | 887243.5884
| 1867 | -32.9657 | 115.2856 | -32.9747 | -33 | 1867 | 77.7917 | 115.2856 | 887358.874
| 1868 | -32.9747 | 115.1387 | -32.9836 | -33 | 1868 | 77.8333 | 115.1387 | 887474.0127
| 1869 | -32.9836 | 114.9921 | -32.9925 | -33 | 1869 | 77.875 | 114.9921 | 887589.0048
| 1870 | -32.9925 | 114.8456 | -33.0015 | -33 | 1870 | 77.9167 | 114.8456 | 887703.8504
| 1871 | -33.0015 | 114.6993 | -33.0104 | -33 | 1871 | 77.9583 | 114.6993 | 887818.5497
| 1872 | -33.0104 | 114.5532 | -33.0193 | -33 | 1872 | 78 | 114.5532 | 887933.1028
| 1873 | -33.0193 | 114.4072 | -33.0282 | -33 | 1873 | 78.0417 | 114.4072 | 888047.51
| 1874 | -33.0282 | 114.2615 | -33.0371 | -33 | 1874 | 78.0833 | 114.2615 | 888161.7715
| 1875 | -33.0371 | 114.1159 | -33.0459 | -33 | 1875 | 78.125 | 114.1159 | 888275.8874
| 1876 | -33.0459 | 113.9705 | -33.0548 | -33.1 | 1876 | 78.1667 | 113.9705 | 888389.858
| 1877 | -33.0548 | 113.8253 | -33.0636 | -33.1 | 1877 | 78.2083 | 113.8253 | 888503.6833
| 1878 | -33.0636 | 113.6803 | -33.0725 | -33.1 | 1878 | 78.25 | 113.6803 | 888617.3637
| 1879 | -33.0725 | 113.5355 | -33.0813 | -33.1 | 1879 | 78.2917 | 113.5355 | 888730.8992
| 1880 | -33.0813 | 113.3909 | -33.0901 | -33.1 | 1880 | 78.3333 | 113.3909 | 888844.2901
| 1881 | -33.0901 | 113.2464 | -33.0989 | -33.1 | 1881 | 78.375 | 113.2464 | 888957.5365
| 1882 | -33.0989 | 113.1022 | -33.1077 | -33.1 | 1882 | 78.4167 | 113.1022 | 889070.6387
| 1883 | -33.1077 | 112.9581 | -33.1165 | -33.1 | 1883 | 78.4583 | 112.9581 | 889183.5968
| 1884 | -33.1165 | 112.8142 | -33.1253 | -33.1 | 1884 | 78.5 | 112.8142 | 889296.4109
| 1885 | -33.1253 | 112.6705 | -33.134 | -33.1 | 1885 | 78.5417 | 112.6705 | 889409.0814
| 1886 | -33.134 | 112.5269 | -33.1428 | -33.1 | 1886 | 78.5833 | 112.5269 | 889521.6084
| 1887 | -33.1428 | 112.3836 | -33.1515 | -33.2 | 1887 | 78.625 | 112.3836 | 889633.9919
| 1888 | -33.1515 | 112.2404 | -33.1602 | -33.2 | 1888 | 78.6667 | 112.2404 | 889746.2324
| 1889 | -33.1602 | 112.0974 | -33.1689 | -33.2 | 1889 | 78.7083 | 112.0974 | 889858.3298
| 1890 | -33.1689 | 111.9546 | -33.1776 | -33.2 | 1890 | 78.75 | 111.9546 | 889970.2844
| 1891 | -33.1776 | 111.812 | -33.1863 | -33.2 | 1891 | 78.7917 | 111.812 | 890082.0964
| 1892 | -33.1863 | 111.6696 | -33.195 | -33.2 | 1892 | 78.8333 | 111.6696 | 890193.766
| 1893 | -33.195 | 111.5273 | -33.2037 | -33.2 | 1893 | 78.875 | 111.5273 | 890305.2933
| 1894 | -33.2037 | 111.3852 | -33.2123 | -33.2 | 1894 | 78.9167 | 111.3852 | 890416.6785
| 1895 | -33.2123 | 111.2433 | -33.221 | -33.2 | 1895 | 78.9583 | 111.2433 | 890527.9218
| 1896 | -33.221 | 111.1016 | -33.2296 | -33.2 | 1896 | 79 | 111.1016 | 890639.0235
| 1897 | -33.2296 | 110.9601 | -33.2382 | -33.2 | 1897 | 79.0417 | 110.9601 | 890749.9835
| 1898 | -33.2382 | 110.8187 | -33.2469 | -33.2 | 1898 | 79.0833 | 110.8187 | 890860.8023
| 1899 | -33.2469 | 110.6776 | -33.2555 | -33.3 | 1899 | 79.125 | 110.6776 | 890971.4798
| 1900 | -33.2555 | 110.5366 | -33.2641 | -33.3 | 1900 | 79.1667 | 110.5366 | 891082.0164
| 1901 | -33.2641 | 110.3957 | -33.2726 | -33.3 | 1901 | 79.2083 | 110.3957 | 891192.4121
| 1902 | -33.2726 | 110.2551 | -33.2812 | -33.3 | 1902 | 79.25 | 110.2551 | 891302.6672
| 1903 | -33.2812 | 110.1146 | -33.2898 | -33.3 | 1903 | 79.2917 | 110.1146 | 891412.7819
| 1904 | -33.2898 | 109.9744 | -33.2983 | -33.3 | 1904 | 79.3333 | 109.9744 | 891522.7563
| 1905 | -33.2983 | 109.8343 | -33.3068 | -33.3 | 1905 | 79.375 | 109.8343 | 891632.5905
| 1906 | -33.3068 | 109.6944 | -33.3154 | -33.3 | 1906 | 79.4167 | 109.6944 | 891742.2849
| 1907 | -33.3154 | 109.5546 | -33.3239 | -33.3 | 1907 | 79.4583 | 109.5546 | 891851.8395
| 1908 | -33.3239 | 109.415 | -33.3324 | -33.3 | 1908 | 79.5 | 109.415 | 891961.2545
| 1909 | -33.3324 | 109.2757 | -33.3409 | -33.3 | 1909 | 79.5417 | 109.2757 | 892070.5302
| 1910 | -33.3409 | 109.1365 | -33.3494 | -33.3 | 1910 | 79.5833 | 109.1365 | 892179.6666
| 1911 | -33.3494 | 108.9974 | -33.3578 | -33.4 | 1911 | 79.625 | 108.9974 | 892288.6641
| 1912 | -33.3578 | 108.8586 | -33.3663 | -33.4 | 1912 | 79.6667 | 108.8586 | 892397.5226
| 1913 | -33.3663 | 108.7199 | -33.3748 | -33.4 | 1913 | 79.7083 | 108.7199 | 892506.2425
| 1914 | -33.3748 | 108.5814 | -33.3832 | -33.4 | 1914 | 79.75 | 108.5814 | 892614.8239
| 1915 | -33.3832 | 108.4431 | -33.3916 | -33.4 | 1915 | 79.7917 | 108.4431 | 892723.267
| 1916 | -33.3916 | 108.3049 | -33.4 | -33.4 | 1916 | 79.8333 | 108.3049 | 892831.5719
| 1917 | -33.4 | 108.1669 | -33.4085 | -33.4 | 1917 | 79.875 | 108.1669 | 892939.7388
| 1918 | -33.4085 | 108.0291 | -33.4168 | -33.4 | 1918 | 79.9167 | 108.0291 | 893047.768
| 1919 | -33.4168 | 107.8915 | -33.4252 | -33.4 | 1919 | 79.9583 | 107.8915 | 893155.6595
| 1920 | -33.4252 | 107.7541 | -33.4336 | -33.4 | 1920 | 80 | 107.7541 | 893263.4136
| 1921 | -33.4336 | 107.6168 | -33.442 | -33.4 | 1921 | 80.0417 | 107.6168 | 893371.0304
| 1922 | -33.442 | 107.4797 | -33.4503 | -33.5 | 1922 | 80.0833 | 107.4797 | 893478.5101
| 1923 | -33.4503 | 107.3428 | -33.4587 | -33.5 | 1923 | 80.125 | 107.3428 | 893585.8529
| 1924 | -33.4587 | 107.206 | -33.467 | -33.5 | 1924 | 80.1667 | 107.206 | 893693.0589
| 1925 | -33.467 | 107.0695 | -33.4753 | -33.5 | 1925 | 80.2083 | 107.0695 | 893800.1284
| 1926 | -33.4753 | 106.9331 | -33.4836 | -33.5 | 1926 | 80.25 | 106.9331 | 893907.0614
| 1927 | -33.4836 | 106.7968 | -33.4919 | -33.5 | 1927 | 80.2917 | 106.7968 | 894013.8583
| 1928 | -33.4919 | 106.6608 | -33.5002 | -33.5 | 1928 | 80.3333 | 106.6608 | 894120.5191
| 1929 | -33.5002 | 106.5249 | -33.5085 | -33.5 | 1929 | 80.375 | 106.5249 | 894227.044
| 1930 | -33.5085 | 106.3892 | -33.5168 | -33.5 | 1930 | 80.4167 | 106.3892 | 894333.4332
| 1931 | -33.5168 | 106.2537 | -33.525 | -33.5 | 1931 | 80.4583 | 106.2537 | 894439.6869
| 1932 | -33.525 | 106.1183 | -33.5333 | -33.5 | 1932 | 80.5 | 106.1183 | 894545.8052
| 1933 | -33.5333 | 105.9831 | -33.5415 | -33.5 | 1933 | 80.5417 | 105.9831 | 894651.7884
| 1934 | -33.5415 | 105.8481 | -33.5498 | -33.5 | 1934 | 80.5833 | 105.8481 | 894757.6365
| 1935 | -33.5498 | 105.7133 | -33.558 | -33.6 | 1935 | 80.625 | 105.7133 | 894863.3498
| 1936 | -33.558 | 105.5786 | -33.5662 | -33.6 | 1936 | 80.6667 | 105.5786 | 894968.9284
| 1937 | -33.5662 | 105.4441 | -33.5744 | -33.6 | 1937 | 80.7083 | 105.4441 | 895074.3725
| 1938 | -33.5744 | 105.3098 | -33.5826 | -33.6 | 1938 | 80.75 | 105.3098 | 895179.6823
| 1939 | -33.5826 | 105.1756 | -33.5907 | -33.6 | 1939 | 80.7917 | 105.1756 | 895284.8579
| 1940 | -33.5907 | 105.0416 | -33.5989 | -33.6 | 1940 | 80.8333 | 105.0416 | 895389.8995
| 1941 | -33.5989 | 104.9078 | -33.6071 | -33.6 | 1941 | 80.875 | 104.9078 | 895494.8073
| 1942 | -33.6071 | 104.7742 | -33.6152 | -33.6 | 1942 | 80.9167 | 104.7742 | 895599.5815
| 1943 | -33.6152 | 104.6407 | -33.6233 | -33.6 | 1943 | 80.9583 | 104.6407 | 895704.2222
| 1944 | -33.6233 | 104.5074 | -33.6315 | -33.6 | 1944 | 81 | 104.5074 | 895808.7296
| 1945 | -33.6315 | 104.3743 | -33.6396 | -33.6 | 1945 | 81.0417 | 104.3743 | 895913.1039
| 1946 | -33.6396 | 104.2413 | -33.6477 | -33.6 | 1946 | 81.0833 | 104.2413 | 896017.3452
| 1947 | -33.6477 | 104.1085 | -33.6558 | -33.7 | 1947 | 81.125 | 104.1085 | 896121.4537
| 1948 | -33.6558 | 103.9759 | -33.6638 | -33.7 | 1948 | 81.1667 | 103.9759 | 896225.4296
| 1949 | -33.6638 | 103.8434 | -33.6719 | -33.7 | 1949 | 81.2083 | 103.8434 | 896329.273
| 1950 | -33.6719 | 103.7111 | -33.68 | -33.7 | 1950 | 81.25 | 103.7111 | 896432.9841
| 1951 | -33.68 | 103.579 | -33.688 | -33.7 | 1951 | 81.2917 | 103.579 | 896536.5631
| 1952 | -33.688 | 103.4471 | -33.6961 | -33.7 | 1952 | 81.3333 | 103.4471 | 896640.0102
| 1953 | -33.6961 | 103.3153 | -33.7041 | -33.7 | 1953 | 81.375 | 103.3153 | 896743.3255
| 1954 | -33.7041 | 103.1837 | -33.7121 | -33.7 | 1954 | 81.4167 | 103.1837 | 896846.5091
| 1955 | -33.7121 | 103.0522 | -33.7201 | -33.7 | 1955 | 81.4583 | 103.0522 | 896949.5614
| 1956 | -33.7201 | 102.9209 | -33.7281 | -33.7 | 1956 | 81.5 | 102.9209 | 897052.4823
| 1957 | -33.7281 | 102.7898 | -33.7361 | -33.7 | 1957 | 81.5417 | 102.7898 | 897155.2721
| 1958 | -33.7361 | 102.6589 | -33.7441 | -33.7 | 1958 | 81.5833 | 102.6589 | 897257.931
| 1959 | -33.7441 | 102.5281 | -33.7521 | -33.8 | 1959 | 81.625 | 102.5281 | 897360.4591
| 1960 | -33.7521 | 102.3975 | -33.76 | -33.8 | 1960 | 81.6667 | 102.3975 | 897462.8566
| 1961 | -33.76 | 102.267 | -33.768 | -33.8 | 1961 | 81.7083 | 102.267 | 897565.1236
| 1962 | -33.768 | 102.1368 | -33.7759 | -33.8 | 1962 | 81.75 | 102.1368 | 897667.2603
| 1963 | -33.7759 | 102.0066 | -33.7839 | -33.8 | 1963 | 81.7917 | 102.0066 | 897769.267
| 1964 | -33.7839 | 101.8767 | -33.7918 | -33.8 | 1964 | 81.8333 | 101.8767 | 897871.1437
| 1965 | -33.7918 | 101.7469 | -33.7997 | -33.8 | 1965 | 81.875 | 101.7469 | 897972.8906
| 1966 | -33.7997 | 101.6173 | -33.8076 | -33.8 | 1966 | 81.9167 | 101.6173 | 898074.5079
| 1967 | -33.8076 | 101.4878 | -33.8155 | -33.8 | 1967 | 81.9583 | 101.4878 | 898175.9957
| 1968 | -33.8155 | 101.3585 | -33.8233 | -33.8 | 1968 | 82 | 101.3585 | 898277.3542
| 1969 | -33.8233 | 101.2294 | -33.8312 | -33.8 | 1969 | 82.0417 | 101.2294 | 898378.5837
| 1970 | -33.8312 | 101.1005 | -33.8391 | -33.8 | 1970 | 82.0833 | 101.1005 | 898479.6841
| 1971 | -33.8391 | 100.9717 | -33.8469 | -33.8 | 1971 | 82.125 | 100.9717 | 898580.6558
| 1972 | -33.8469 | 100.843 | -33.8548 | -33.9 | 1972 | 82.1667 | 100.843 | 898681.4988
| 1973 | -33.8548 | 100.7146 | -33.8626 | -33.9 | 1973 | 82.2083 | 100.7146 | 898782.2134
| 1974 | -33.8626 | 100.5863 | -33.8704 | -33.9 | 1974 | 82.25 | 100.5863 | 898882.7997
| 1975 | -33.8704 | 100.4581 | -33.8782 | -33.9 | 1975 | 82.2917 | 100.4581 | 898983.2578
| 1976 | -33.8782 | 100.3302 | -33.886 | -33.9 | 1976 | 82.3333 | 100.3302 | 899083.588
| 1977 | -33.886 | 100.2023 | -33.8938 | -33.9 | 1977 | 82.375 | 100.2023 | 899183.7903
| 1978 | -33.8938 | 100.0747 | -33.9016 | -33.9 | 1978 | 82.4167 | 100.0747 | 899283.865
| 1979 | -33.9016 | 99.9472 | -33.9094 | -33.9 | 1979 | 82.4583 | 99.9472 | 899383.8122

## Insulated Shed
How long will it take for my water storage to reach freezing temperatures? | [8 empty] | Initial Heat in tank (BTU) | 51460
Note: Cubic Tank Calculations; Non-windy conditions only. | [8 empty] | Heat in water = 8.3 BTU/degF-Gal
User Inputs
Tank Size (gal) | 1550 | [7 empty] | rb | 3.625 | ft
Temperature of water at fillup (deg F) | 36 | [7 empty] | rc | 3.7917 | ft
Freezing Temp (deg F) | 32 | [7 empty] | ln(rc/rb) | 0.044951 | unitless
Outside temp (deg F) | -40 | [7 empty] | kinsulation | 0.013889 | (BTU-ft/(hr-ft2-F)
Height of tank (ft) | 5.4167 | [7 empty] | GrPr (air, -40F) | 10^10
Diameter of Tank (ft) | 7.25 | [7 empty] | h (cylinder) | 0.80481
R-value per inch of Insulation | 6 | [7 empty] | Thermal conductivity of insulation (BTU-ft/(hr-ft2-F) | 0.013889
Thickness of insulation (inches) | 2
How much heat was lost during this time? (total BTUs) | 51460
How many hours until danger zone? | 41
How many days? | 1.7083
If "#N/A" appears, adjust outside temp and or Insulation values.
| Time (hrs) | T1 | Heat lost to environment (BTU/hr) | Temperature of water after 1 hr | Rounded Temp (F) | Time (hrs) | Time (days)
| 0 | 36 | 1245.5671 | 35.9032 | 35.9 | 0 | 0
| 1 | 35.9032 | 1243.9803 | 35.8065 | 35.8 | 1 | 0.041667
| 2 | 35.8065 | 1242.3956 | 35.7099 | 35.7 | 2 | 0.083333
| 3 | 35.7099 | 1240.8129 | 35.6135 | 35.6 | 3 | 0.125
| 4 | 35.6135 | 1239.2322 | 35.5171 | 35.5 | 4 | 0.16667
| 5 | 35.5171 | 1237.6535 | 35.4209 | 35.4 | 5 | 0.20833
| 6 | 35.4209 | 1236.0768 | 35.3249 | 35.3 | 6 | 0.25
| 7 | 35.3249 | 1234.5021 | 35.2289 | 35.2 | 7 | 0.29167
| 8 | 35.2289 | 1232.9295 | 35.1331 | 35.1 | 8 | 0.33333
| 9 | 35.1331 | 1231.3588 | 35.0373 | 35 | 9 | 0.375
| 10 | 35.0373 | 1229.7902 | 34.9418 | 34.9 | 10 | 0.41667
| 11 | 34.9418 | 1228.2235 | 34.8463 | 34.8 | 11 | 0.45833
| 12 | 34.8463 | 1226.6588 | 34.7509 | 34.8 | 12 | 0.5
| 13 | 34.7509 | 1225.0962 | 34.6557 | 34.7 | 13 | 0.54167
| 14 | 34.6557 | 1223.5355 | 34.5606 | 34.6 | 14 | 0.58333
| 15 | 34.5606 | 1221.9768 | 34.4656 | 34.5 | 15 | 0.625
| 16 | 34.4656 | 1220.4201 | 34.3708 | 34.4 | 16 | 0.66667
| 17 | 34.3708 | 1218.8654 | 34.276 | 34.3 | 17 | 0.70833
| 18 | 34.276 | 1217.3126 | 34.1814 | 34.2 | 18 | 0.75
| 19 | 34.1814 | 1215.7619 | 34.0869 | 34.1 | 19 | 0.79167
| 20 | 34.0869 | 1214.2131 | 33.9925 | 34 | 20 | 0.83333
| 21 | 33.9925 | 1212.6663 | 33.8982 | 33.9 | 21 | 0.875
| 22 | 33.8982 | 1211.1214 | 33.8041 | 33.8 | 22 | 0.91667
| 23 | 33.8041 | 1209.5785 | 33.7101 | 33.7 | 23 | 0.95833
| 24 | 33.7101 | 1208.0376 | 33.6162 | 33.6 | 24 | 1
| 25 | 33.6162 | 1206.4987 | 33.5224 | 33.5 | 25 | 1.0417
| 26 | 33.5224 | 1204.9617 | 33.4287 | 33.4 | 26 | 1.0833
| 27 | 33.4287 | 1203.4267 | 33.3352 | 33.3 | 27 | 1.125
| 28 | 33.3352 | 1201.8936 | 33.2418 | 33.2 | 28 | 1.1667
| 29 | 33.2418 | 1200.3625 | 33.1485 | 33.1 | 29 | 1.2083
| 30 | 33.1485 | 1198.8333 | 33.0553 | 33.1 | 30 | 1.25
| 31 | 33.0553 | 1197.3061 | 32.9622 | 33 | 31 | 1.2917
| 32 | 32.9622 | 1195.7808 | 32.8693 | 32.9 | 32 | 1.3333
| 33 | 32.8693 | 1194.2574 | 32.7764 | 32.8 | 33 | 1.375
| 34 | 32.7764 | 1192.7361 | 32.6837 | 32.7 | 34 | 1.4167
| 35 | 32.6837 | 1191.2166 | 32.5911 | 32.6 | 35 | 1.4583
| 36 | 32.5911 | 1189.6991 | 32.4987 | 32.5 | 36 | 1.5
| 37 | 32.4987 | 1188.1835 | 32.4063 | 32.4 | 37 | 1.5417
| 38 | 32.4063 | 1186.6698 | 32.3141 | 32.3 | 38 | 1.5833
| 39 | 32.3141 | 1185.1581 | 32.2219 | 32.2 | 39 | 1.625
| 40 | 32.2219 | 1183.6483 | 32.1299 | 32.1 | 40 | 1.6667
| 41 | 32.1299 | 1182.1404 | 32.038 | 32 | 41 | 1.7083
| 42 | 32.038 | 1180.6345 | 31.9463 | 31.9 | 42 | 1.75
| 43 | 31.9463 | 1179.1304 | 31.8546 | 31.9 | 43 | 1.7917
| 44 | 31.8546 | 1177.6283 | 31.7631 | 31.8 | 44 | 1.8333
| 45 | 31.7631 | 1176.1281 | 31.6717 | 31.7 | 45 | 1.875
| 46 | 31.6717 | 1174.6298 | 31.5804 | 31.6 | 46 | 1.9167
| 47 | 31.5804 | 1173.1334 | 31.4892 | 31.5 | 47 | 1.9583
| 48 | 31.4892 | 1171.6389 | 31.3981 | 31.4 | 48 | 2
| 49 | 31.3981 | 1170.1463 | 31.3071 | 31.3 | 49 | 2.0417
| 50 | 31.3071 | 1168.6557 | 31.2163 | 31.2 | 50 | 2.0833
| 51 | 31.2163 | 1167.1669 | 31.1256 | 31.1 | 51 | 2.125
| 52 | 31.1256 | 1165.68 | 31.035 | 31 | 52 | 2.1667
| 53 | 31.035 | 1164.195 | 30.9445 | 30.9 | 53 | 2.2083
| 54 | 30.9445 | 1162.7119 | 30.8541 | 30.9 | 54 | 2.25
| 55 | 30.8541 | 1161.2307 | 30.7638 | 30.8 | 55 | 2.2917
| 56 | 30.7638 | 1159.7514 | 30.6737 | 30.7 | 56 | 2.3333
| 57 | 30.6737 | 1158.274 | 30.5837 | 30.6 | 57 | 2.375
| 58 | 30.5837 | 1156.7984 | 30.4937 | 30.5 | 58 | 2.4167
| 59 | 30.4937 | 1155.3247 | 30.4039 | 30.4 | 59 | 2.4583
| 60 | 30.4039 | 1153.8529 | 30.3142 | 30.3 | 60 | 2.5
| 61 | 30.3142 | 1152.383 | 30.2247 | 30.2 | 61 | 2.5417
| 62 | 30.2247 | 1150.915 | 30.1352 | 30.1 | 62 | 2.5833
| 63 | 30.1352 | 1149.4488 | 30.0459 | 30 | 63 | 2.625
| 64 | 30.0459 | 1147.9845 | 29.9566 | 30 | 64 | 2.6667
| 65 | 29.9566 | 1146.522 | 29.8675 | 29.9 | 65 | 2.7083
| 66 | 29.8675 | 1145.0614 | 29.7785 | 29.8 | 66 | 2.75
| 67 | 29.7785 | 1143.6027 | 29.6896 | 29.7 | 67 | 2.7917
| 68 | 29.6896 | 1142.1459 | 29.6008 | 29.6 | 68 | 2.8333
| 69 | 29.6008 | 1140.6908 | 29.5122 | 29.5 | 69 | 2.875
| 70 | 29.5122 | 1139.2377 | 29.4236 | 29.4 | 70 | 2.9167
| 71 | 29.4236 | 1137.7864 | 29.3352 | 29.3 | 71 | 2.9583
| 72 | 29.3352 | 1136.3369 | 29.2468 | 29.2 | 72 | 3
| 73 | 29.2468 | 1134.8893 | 29.1586 | 29.2 | 73 | 3.0417
| 74 | 29.1586 | 1133.4436 | 29.0705 | 29.1 | 74 | 3.0833
| 75 | 29.0705 | 1131.9996 | 28.9825 | 29 | 75 | 3.125
| 76 | 28.9825 | 1130.5576 | 28.8947 | 28.9 | 76 | 3.1667
| 77 | 28.8947 | 1129.1173 | 28.8069 | 28.8 | 77 | 3.2083
| 78 | 28.8069 | 1127.6789 | 28.7192 | 28.7 | 78 | 3.25
| 79 | 28.7192 | 1126.2423 | 28.6317 | 28.6 | 79 | 3.2917
| 80 | 28.6317 | 1124.8076 | 28.5443 | 28.5 | 80 | 3.3333
| 81 | 28.5443 | 1123.3747 | 28.4569 | 28.5 | 81 | 3.375
| 82 | 28.4569 | 1121.9436 | 28.3697 | 28.4 | 82 | 3.4167
| 83 | 28.3697 | 1120.5143 | 28.2826 | 28.3 | 83 | 3.4583
| 84 | 28.2826 | 1119.0868 | 28.1956 | 28.2 | 84 | 3.5
| 85 | 28.1956 | 1117.6612 | 28.1088 | 28.1 | 85 | 3.5417
| 86 | 28.1088 | 1116.2374 | 28.022 | 28 | 86 | 3.5833
| 87 | 28.022 | 1114.8154 | 27.9353 | 27.9 | 87 | 3.625
| 88 | 27.9353 | 1113.3952 | 27.8488 | 27.8 | 88 | 3.6667
| 89 | 27.8488 | 1111.9768 | 27.7624 | 27.8 | 89 | 3.7083
| 90 | 27.7624 | 1110.5602 | 27.676 | 27.7 | 90 | 3.75
| 91 | 27.676 | 1109.1455 | 27.5898 | 27.6 | 91 | 3.7917
| 92 | 27.5898 | 1107.7325 | 27.5037 | 27.5 | 92 | 3.8333
| 93 | 27.5037 | 1106.3213 | 27.4177 | 27.4 | 93 | 3.875
| 94 | 27.4177 | 1104.912 | 27.3318 | 27.3 | 94 | 3.9167
| 95 | 27.3318 | 1103.5044 | 27.2461 | 27.2 | 95 | 3.9583
| 96 | 27.2461 | 1102.0986 | 27.1604 | 27.2 | 96 | 4
| 97 | 27.1604 | 1100.6946 | 27.0748 | 27.1 | 97 | 4.0417
| 98 | 27.0748 | 1099.2924 | 26.9894 | 27 | 98 | 4.0833
| 99 | 26.9894 | 1097.892 | 26.9041 | 26.9 | 99 | 4.125
| 100 | 26.9041 | 1096.4934 | 26.8188 | 26.8 | 100 | 4.1667
| 101 | 26.8188 | 1095.0965 | 26.7337 | 26.7 | 101 | 4.2083
| 102 | 26.7337 | 1093.7015 | 26.6487 | 26.6 | 102 | 4.25
| 103 | 26.6487 | 1092.3082 | 26.5638 | 26.6 | 103 | 4.2917
| 104 | 26.5638 | 1090.9166 | 26.479 | 26.5 | 104 | 4.3333
| 105 | 26.479 | 1089.5269 | 26.3943 | 26.4 | 105 | 4.375
| 106 | 26.3943 | 1088.1389 | 26.3097 | 26.3 | 106 | 4.4167
| 107 | 26.3097 | 1086.7527 | 26.2252 | 26.2 | 107 | 4.4583
| 108 | 26.2252 | 1085.3683 | 26.1409 | 26.1 | 108 | 4.5
| 109 | 26.1409 | 1083.9856 | 26.0566 | 26.1 | 109 | 4.5417
| 110 | 26.0566 | 1082.6047 | 25.9725 | 26 | 110 | 4.5833
| 111 | 25.9725 | 1081.2255 | 25.8884 | 25.9 | 111 | 4.625
| 112 | 25.8884 | 1079.8481 | 25.8045 | 25.8 | 112 | 4.6667
| 113 | 25.8045 | 1078.4725 | 25.7207 | 25.7 | 113 | 4.7083
| 114 | 25.7207 | 1077.0986 | 25.6369 | 25.6 | 114 | 4.75
| 115 | 25.6369 | 1075.7264 | 25.5533 | 25.6 | 115 | 4.7917
| 116 | 25.5533 | 1074.356 | 25.4698 | 25.5 | 116 | 4.8333
| 117 | 25.4698 | 1072.9874 | 25.3864 | 25.4 | 117 | 4.875
| 118 | 25.3864 | 1071.6205 | 25.3031 | 25.3 | 118 | 4.9167
| 119 | 25.3031 | 1070.2553 | 25.2199 | 25.2 | 119 | 4.9583
| 120 | 25.2199 | 1068.8919 | 25.1368 | 25.1 | 120 | 5
| 121 | 25.1368 | 1067.5302 | 25.0539 | 25.1 | 121 | 5.0417
| 122 | 25.0539 | 1066.1703 | 24.971 | 25 | 122 | 5.0833
| 123 | 24.971 | 1064.812 | 24.8882 | 24.9 | 123 | 5.125
| 124 | 24.8882 | 1063.4556 | 24.8055 | 24.8 | 124 | 5.1667
| 125 | 24.8055 | 1062.1008 | 24.723 | 24.7 | 125 | 5.2083
| 126 | 24.723 | 1060.7478 | 24.6405 | 24.6 | 126 | 5.25
| 127 | 24.6405 | 1059.3964 | 24.5582 | 24.6 | 127 | 5.2917
| 128 | 24.5582 | 1058.0469 | 24.476 | 24.5 | 128 | 5.3333
| 129 | 24.476 | 1056.699 | 24.3938 | 24.4 | 129 | 5.375
| 130 | 24.3938 | 1055.3528 | 24.3118 | 24.3 | 130 | 5.4167
| 131 | 24.3118 | 1054.0084 | 24.2299 | 24.2 | 131 | 5.4583
| 132 | 24.2299 | 1052.6657 | 24.148 | 24.1 | 132 | 5.5
| 133 | 24.148 | 1051.3246 | 24.0663 | 24.1 | 133 | 5.5417
| 134 | 24.0663 | 1049.9853 | 23.9847 | 24 | 134 | 5.5833
| 135 | 23.9847 | 1048.6477 | 23.9032 | 23.9 | 135 | 5.625
| 136 | 23.9032 | 1047.3118 | 23.8218 | 23.8 | 136 | 5.6667
| 137 | 23.8218 | 1045.9776 | 23.7405 | 23.7 | 137 | 5.7083
| 138 | 23.7405 | 1044.6451 | 23.6593 | 23.7 | 138 | 5.75
| 139 | 23.6593 | 1043.3143 | 23.5782 | 23.6 | 139 | 5.7917
| 140 | 23.5782 | 1041.9852 | 23.4972 | 23.5 | 140 | 5.8333
| 141 | 23.4972 | 1040.6578 | 23.4163 | 23.4 | 141 | 5.875
| 142 | 23.4163 | 1039.3321 | 23.3355 | 23.3 | 142 | 5.9167
| 143 | 23.3355 | 1038.0081 | 23.2548 | 23.3 | 143 | 5.9583
| 144 | 23.2548 | 1036.6857 | 23.1742 | 23.2 | 144 | 6
| 145 | 23.1742 | 1035.3651 | 23.0938 | 23.1 | 145 | 6.0417
| 146 | 23.0938 | 1034.0461 | 23.0134 | 23 | 146 | 6.0833
| 147 | 23.0134 | 1032.7288 | 22.9331 | 22.9 | 147 | 6.125
| 148 | 22.9331 | 1031.4132 | 22.8529 | 22.9 | 148 | 6.1667
| 149 | 22.8529 | 1030.0992 | 22.7729 | 22.8 | 149 | 6.2083
| 150 | 22.7729 | 1028.787 | 22.6929 | 22.7 | 150 | 6.25
| 151 | 22.6929 | 1027.4764 | 22.613 | 22.6 | 151 | 6.2917
| 152 | 22.613 | 1026.1674 | 22.5333 | 22.5 | 152 | 6.3333
| 153 | 22.5333 | 1024.8602 | 22.4536 | 22.5 | 153 | 6.375
| 154 | 22.4536 | 1023.5546 | 22.374 | 22.4 | 154 | 6.4167
| 155 | 22.374 | 1022.2507 | 22.2946 | 22.3 | 155 | 6.4583
| 156 | 22.2946 | 1020.9484 | 22.2152 | 22.2 | 156 | 6.5
| 157 | 22.2152 | 1019.6478 | 22.136 | 22.1 | 157 | 6.5417
| 158 | 22.136 | 1018.3488 | 22.0568 | 22.1 | 158 | 6.5833
| 159 | 22.0568 | 1017.0515 | 21.9778 | 22 | 159 | 6.625
| 160 | 21.9778 | 1015.7559 | 21.8988 | 21.9 | 160 | 6.6667
| 161 | 21.8988 | 1014.4619 | 21.8199 | 21.8 | 161 | 6.7083
| 162 | 21.8199 | 1013.1695 | 21.7412 | 21.7 | 162 | 6.75
| 163 | 21.7412 | 1011.8788 | 21.6625 | 21.7 | 163 | 6.7917
| 164 | 21.6625 | 1010.5898 | 21.584 | 21.6 | 164 | 6.8333
| 165 | 21.584 | 1009.3024 | 21.5055 | 21.5 | 165 | 6.875
40 | 166 | 21.5055 | 1008.0166 | 21.4272 | 21.4 | 166 | 6.9167
#N/A | 167 | 21.4272 | 1006.7324 | 21.3489 | 21.3 | 167 | 6.9583
41 | 168 | 21.3489 | 1005.4499 | 21.2708 | 21.3 | 168 | 7
| 169 | 21.2708 | 1004.1691 | 21.1927 | 21.2 | 169 | 7.0417
| 170 | 21.1927 | 1002.8898 | 21.1148 | 21.1 | 170 | 7.0833
| 171 | 21.1148 | 1001.6122 | 21.0369 | 21 | 171 | 7.125
| 172 | 21.0369 | 1000.3363 | 20.9591 | 21 | 172 | 7.1667
| 173 | 20.9591 | 999.0619 | 20.8815 | 20.9 | 173 | 7.2083
| 174 | 20.8815 | 997.7892 | 20.8039 | 20.8 | 174 | 7.25
| 175 | 20.8039 | 996.5181 | 20.7265 | 20.7 | 175 | 7.2917
| 176 | 20.7265 | 995.2486 | 20.6491 | 20.6 | 176 | 7.3333
| 177 | 20.6491 | 993.9807 | 20.5718 | 20.6 | 177 | 7.375
| 178 | 20.5718 | 992.7144 | 20.4947 | 20.5 | 178 | 7.4167
| 179 | 20.4947 | 991.4498 | 20.4176 | 20.4 | 179 | 7.4583
| 180 | 20.4176 | 990.1868 | 20.3406 | 20.3 | 180 | 7.5
| 181 | 20.3406 | 988.9253 | 20.2638 | 20.3 | 181 | 7.5417
| 182 | 20.2638 | 987.6655 | 20.187 | 20.2 | 182 | 7.5833
| 183 | 20.187 | 986.4073 | 20.1103 | 20.1 | 183 | 7.625
| 184 | 20.1103 | 985.1507 | 20.0338 | 20 | 184 | 7.6667
| 185 | 20.0338 | 983.8957 | 19.9573 | 20 | 185 | 7.7083
| 186 | 19.9573 | 982.6423 | 19.8809 | 19.9 | 186 | 7.75
| 187 | 19.8809 | 981.3905 | 19.8046 | 19.8 | 187 | 7.7917
| 188 | 19.8046 | 980.1403 | 19.7284 | 19.7 | 188 | 7.8333
| 189 | 19.7284 | 978.8916 | 19.6523 | 19.7 | 189 | 7.875
| 190 | 19.6523 | 977.6446 | 19.5763 | 19.6 | 190 | 7.9167
| 191 | 19.5763 | 976.3992 | 19.5005 | 19.5 | 191 | 7.9583
| 192 | 19.5005 | 975.1553 | 19.4247 | 19.4 | 192 | 8
| 193 | 19.4247 | 973.913 | 19.3489 | 19.3 | 193 | 8.0417
| 194 | 19.3489 | 972.6723 | 19.2733 | 19.3 | 194 | 8.0833
| 195 | 19.2733 | 971.4332 | 19.1978 | 19.2 | 195 | 8.125
| 196 | 19.1978 | 970.1957 | 19.1224 | 19.1 | 196 | 8.1667
| 197 | 19.1224 | 968.9597 | 19.0471 | 19 | 197 | 8.2083
| 198 | 19.0471 | 967.7254 | 18.9719 | 19 | 198 | 8.25
| 199 | 18.9719 | 966.4925 | 18.8968 | 18.9 | 199 | 8.2917
| 200 | 18.8968 | 965.2613 | 18.8217 | 18.8 | 200 | 8.3333
| 201 | 18.8217 | 964.0316 | 18.7468 | 18.7 | 201 | 8.375
| 202 | 18.7468 | 962.8035 | 18.672 | 18.7 | 202 | 8.4167
| 203 | 18.672 | 961.577 | 18.5972 | 18.6 | 203 | 8.4583
| 204 | 18.5972 | 960.352 | 18.5226 | 18.5 | 204 | 8.5
| 205 | 18.5226 | 959.1286 | 18.448 | 18.4 | 205 | 8.5417
| 206 | 18.448 | 957.9067 | 18.3735 | 18.4 | 206 | 8.5833
| 207 | 18.3735 | 956.6864 | 18.2992 | 18.3 | 207 | 8.625
| 208 | 18.2992 | 955.4677 | 18.2249 | 18.2 | 208 | 8.6667
| 209 | 18.2249 | 954.2505 | 18.1507 | 18.2 | 209 | 8.7083
| 210 | 18.1507 | 953.0349 | 18.0767 | 18.1 | 210 | 8.75
| 211 | 18.0767 | 951.8208 | 18.0027 | 18 | 211 | 8.7917
| 212 | 18.0027 | 950.6082 | 17.9288 | 17.9 | 212 | 8.8333
| 213 | 17.9288 | 949.3972 | 17.855 | 17.9 | 213 | 8.875
| 214 | 17.855 | 948.1877 | 17.7813 | 17.8 | 214 | 8.9167
| 215 | 17.7813 | 946.9798 | 17.7077 | 17.7 | 215 | 8.9583
| 216 | 17.7077 | 945.7734 | 17.6342 | 17.6 | 216 | 9
| 217 | 17.6342 | 944.5686 | 17.5607 | 17.6 | 217 | 9.0417
| 218 | 17.5607 | 943.3653 | 17.4874 | 17.5 | 218 | 9.0833
| 219 | 17.4874 | 942.1635 | 17.4142 | 17.4 | 219 | 9.125
| 220 | 17.4142 | 940.9633 | 17.341 | 17.3 | 220 | 9.1667
| 221 | 17.341 | 939.7646 | 17.268 | 17.3 | 221 | 9.2083
| 222 | 17.268 | 938.5674 | 17.195 | 17.2 | 222 | 9.25
| 223 | 17.195 | 937.3717 | 17.1222 | 17.1 | 223 | 9.2917
| 224 | 17.1222 | 936.1776 | 17.0494 | 17 | 224 | 9.3333
| 225 | 17.0494 | 934.9849 | 16.9767 | 17 | 225 | 9.375
| 226 | 16.9767 | 933.7938 | 16.9041 | 16.9 | 226 | 9.4167
| 227 | 16.9041 | 932.6043 | 16.8316 | 16.8 | 227 | 9.4583
| 228 | 16.8316 | 931.4162 | 16.7592 | 16.8 | 228 | 9.5
| 229 | 16.7592 | 930.2296 | 16.6869 | 16.7 | 229 | 9.5417
| 230 | 16.6869 | 929.0446 | 16.6147 | 16.6 | 230 | 9.5833
| 231 | 16.6147 | 927.8611 | 16.5426 | 16.5 | 231 | 9.625
| 232 | 16.5426 | 926.679 | 16.4706 | 16.5 | 232 | 9.6667
| 233 | 16.4706 | 925.4985 | 16.3986 | 16.4 | 233 | 9.7083
| 234 | 16.3986 | 924.3195 | 16.3268 | 16.3 | 234 | 9.75
| 235 | 16.3268 | 923.142 | 16.255 | 16.3 | 235 | 9.7917
| 236 | 16.255 | 921.966 | 16.1834 | 16.2 | 236 | 9.8333
| 237 | 16.1834 | 920.7915 | 16.1118 | 16.1 | 237 | 9.875
| 238 | 16.1118 | 919.6184 | 16.0403 | 16 | 238 | 9.9167
| 239 | 16.0403 | 918.4469 | 15.9689 | 16 | 239 | 9.9583
| 240 | 15.9689 | 917.2769 | 15.8976 | 15.9 | 240 | 10
| 241 | 15.8976 | 916.1083 | 15.8264 | 15.8 | 241 | 10.0417
| 242 | 15.8264 | 914.9413 | 15.7553 | 15.8 | 242 | 10.0833
| 243 | 15.7553 | 913.7757 | 15.6843 | 15.7 | 243 | 10.125
| 244 | 15.6843 | 912.6116 | 15.6133 | 15.6 | 244 | 10.1667
| 245 | 15.6133 | 911.449 | 15.5425 | 15.5 | 245 | 10.2083
| 246 | 15.5425 | 910.2879 | 15.4717 | 15.5 | 246 | 10.25
| 247 | 15.4717 | 909.1283 | 15.4011 | 15.4 | 247 | 10.2917
| 248 | 15.4011 | 907.9701 | 15.3305 | 15.3 | 248 | 10.3333
| 249 | 15.3305 | 906.8134 | 15.26 | 15.3 | 249 | 10.375
| 250 | 15.26 | 905.6582 | 15.1896 | 15.2 | 250 | 10.4167
| 251 | 15.1896 | 904.5045 | 15.1193 | 15.1 | 251 | 10.4583
| 252 | 15.1193 | 903.3522 | 15.0491 | 15 | 252 | 10.5
| 253 | 15.0491 | 902.2014 | 14.9789 | 15 | 253 | 10.5417
| 254 | 14.9789 | 901.0521 | 14.9089 | 14.9 | 254 | 10.5833
| 255 | 14.9089 | 899.9042 | 14.839 | 14.8 | 255 | 10.625
| 256 | 14.839 | 898.7578 | 14.7691 | 14.8 | 256 | 10.6667
| 257 | 14.7691 | 897.6128 | 14.6993 | 14.7 | 257 | 10.7083
| 258 | 14.6993 | 896.4694 | 14.6296 | 14.6 | 258 | 10.75
| 259 | 14.6296 | 895.3273 | 14.56 | 14.6 | 259 | 10.7917
| 260 | 14.56 | 894.1867 | 14.4905 | 14.5 | 260 | 10.8333
| 261 | 14.4905 | 893.0476 | 14.4211 | 14.4 | 261 | 10.875
| 262 | 14.4211 | 891.9099 | 14.3518 | 14.4 | 262 | 10.9167
| 263 | 14.3518 | 890.7737 | 14.2826 | 14.3 | 263 | 10.9583
| 264 | 14.2826 | 889.6389 | 14.2134 | 14.2 | 264 | 11
| 265 | 14.2134 | 888.5056 | 14.1443 | 14.1 | 265 | 11.0417
| 266 | 14.1443 | 887.3737 | 14.0754 | 14.1 | 266 | 11.0833
| 267 | 14.0754 | 886.2433 | 14.0065 | 14 | 267 | 11.125
| 268 | 14.0065 | 885.1143 | 13.9377 | 13.9 | 268 | 11.1667
| 269 | 13.9377 | 883.9867 | 13.869 | 13.9 | 269 | 11.2083
| 270 | 13.869 | 882.8606 | 13.8003 | 13.8 | 270 | 11.25
| 271 | 13.8003 | 881.7359 | 13.7318 | 13.7 | 271 | 11.2917
| 272 | 13.7318 | 880.6126 | 13.6633 | 13.7 | 272 | 11.3333
| 273 | 13.6633 | 879.4908 | 13.595 | 13.6 | 273 | 11.375
| 274 | 13.595 | 878.3704 | 13.5267 | 13.5 | 274 | 11.4167
| 275 | 13.5267 | 877.2514 | 13.4585 | 13.5 | 275 | 11.4583
| 276 | 13.4585 | 876.1338 | 13.3904 | 13.4 | 276 | 11.5
| 277 | 13.3904 | 875.0177 | 13.3224 | 13.3 | 277 | 11.5417
| 278 | 13.3224 | 873.903 | 13.2545 | 13.3 | 278 | 11.5833
| 279 | 13.2545 | 872.7897 | 13.1866 | 13.2 | 279 | 11.625
| 280 | 13.1866 | 871.6778 | 13.1189 | 13.1 | 280 | 11.6667
| 281 | 13.1189 | 870.5674 | 13.0512 | 13.1 | 281 | 11.7083
| 282 | 13.0512 | 869.4583 | 12.9836 | 13 | 282 | 11.75
| 283 | 12.9836 | 868.3507 | 12.9161 | 12.9 | 283 | 11.7917
| 284 | 12.9161 | 867.2445 | 12.8487 | 12.8 | 284 | 11.8333
| 285 | 12.8487 | 866.1397 | 12.7814 | 12.8 | 285 | 11.875
| 286 | 12.7814 | 865.0363 | 12.7141 | 12.7 | 286 | 11.9167
| 287 | 12.7141 | 863.9343 | 12.647 | 12.6 | 287 | 11.9583
| 288 | 12.647 | 862.8337 | 12.5799 | 12.6 | 288 | 12
| 289 | 12.5799 | 861.7345 | 12.5129 | 12.5 | 289 | 12.0417
| 290 | 12.5129 | 860.6368 | 12.446 | 12.4 | 290 | 12.0833
| 291 | 12.446 | 859.5404 | 12.3792 | 12.4 | 291 | 12.125
| 292 | 12.3792 | 858.4454 | 12.3125 | 12.3 | 292 | 12.1667
| 293 | 12.3125 | 857.3518 | 12.2459 | 12.2 | 293 | 12.2083
| 294 | 12.2459 | 856.2596 | 12.1793 | 12.2 | 294 | 12.25
| 295 | 12.1793 | 855.1688 | 12.1128 | 12.1 | 295 | 12.2917
| 296 | 12.1128 | 854.0794 | 12.0464 | 12 | 296 | 12.3333
| 297 | 12.0464 | 852.9913 | 11.9801 | 12 | 297 | 12.375
| 298 | 11.9801 | 851.9047 | 11.9139 | 11.9 | 298 | 12.4167
| 299 | 11.9139 | 850.8194 | 11.8478 | 11.8 | 299 | 12.4583
| 300 | 11.8478 | 849.7355 | 11.7817 | 11.8 | 300 | 12.5
| 301 | 11.7817 | 848.653 | 11.7158 | 11.7 | 301 | 12.5417
| 302 | 11.7158 | 847.5719 | 11.6499 | 11.6 | 302 | 12.5833
| 303 | 11.6499 | 846.4922 | 11.5841 | 11.6 | 303 | 12.625
| 304 | 11.5841 | 845.4138 | 11.5184 | 11.5 | 304 | 12.6667
| 305 | 11.5184 | 844.3368 | 11.4527 | 11.5 | 305 | 12.7083
| 306 | 11.4527 | 843.2612 | 11.3872 | 11.4 | 306 | 12.75
| 307 | 11.3872 | 842.1869 | 11.3217 | 11.3 | 307 | 12.7917
| 308 | 11.3217 | 841.1141 | 11.2564 | 11.3 | 308 | 12.8333
| 309 | 11.2564 | 840.0425 | 11.1911 | 11.2 | 309 | 12.875
| 310 | 11.1911 | 838.9724 | 11.1258 | 11.1 | 310 | 12.9167
| 311 | 11.1258 | 837.9036 | 11.0607 | 11.1 | 311 | 12.9583
| 312 | 11.0607 | 836.8362 | 10.9957 | 11 | 312 | 13
| 313 | 10.9957 | 835.7701 | 10.9307 | 10.9 | 313 | 13.0417
| 314 | 10.9307 | 834.7054 | 10.8658 | 10.9 | 314 | 13.0833
| 315 | 10.8658 | 833.6421 | 10.801 | 10.8 | 315 | 13.125
| 316 | 10.801 | 832.5801 | 10.7363 | 10.7 | 316 | 13.1667
| 317 | 10.7363 | 831.5194 | 10.6717 | 10.7 | 317 | 13.2083
| 318 | 10.6717 | 830.4601 | 10.6071 | 10.6 | 318 | 13.25
| 319 | 10.6071 | 829.4022 | 10.5427 | 10.5 | 319 | 13.2917
| 320 | 10.5427 | 828.3456 | 10.4783 | 10.5 | 320 | 13.3333
| 321 | 10.4783 | 827.2903 | 10.414 | 10.4 | 321 | 13.375
| 322 | 10.414 | 826.2364 | 10.3497 | 10.3 | 322 | 13.4167
| 323 | 10.3497 | 825.1839 | 10.2856 | 10.3 | 323 | 13.4583
| 324 | 10.2856 | 824.1326 | 10.2215 | 10.2 | 324 | 13.5
| 325 | 10.2215 | 823.0828 | 10.1576 | 10.2 | 325 | 13.5417
| 326 | 10.1576 | 822.0342 | 10.0937 | 10.1 | 326 | 13.5833
| 327 | 10.0937 | 820.987 | 10.0298 | 10 | 327 | 13.625
| 328 | 10.0298 | 819.9411 | 9.9661 | 10 | 328 | 13.6667
| 329 | 9.9661 | 818.8966 | 9.9025 | 9.9 | 329 | 13.7083
| 330 | 9.9025 | 817.8534 | 9.8389 | 9.8 | 330 | 13.75
| 331 | 9.8389 | 816.8115 | 9.7754 | 9.8 | 331 | 13.7917
| 332 | 9.7754 | 815.7709 | 9.712 | 9.7 | 332 | 13.8333
| 333 | 9.712 | 814.7317 | 9.6487 | 9.6 | 333 | 13.875
| 334 | 9.6487 | 813.6938 | 9.5854 | 9.6 | 334 | 13.9167
| 335 | 9.5854 | 812.6572 | 9.5222 | 9.5 | 335 | 13.9583
| 336 | 9.5222 | 811.6219 | 9.4591 | 9.5 | 336 | 14
| 337 | 9.4591 | 810.588 | 9.3961 | 9.4 | 337 | 14.0417
| 338 | 9.3961 | 809.5554 | 9.3332 | 9.3 | 338 | 14.0833
| 339 | 9.3332 | 808.5241 | 9.2704 | 9.3 | 339 | 14.125
| 340 | 9.2704 | 807.4941 | 9.2076 | 9.2 | 340 | 14.1667
| 341 | 9.2076 | 806.4654 | 9.1449 | 9.1 | 341 | 14.2083
| 342 | 9.1449 | 805.438 | 9.0823 | 9.1 | 342 | 14.25
| 343 | 9.0823 | 804.4119 | 9.0198 | 9 | 343 | 14.2917
| 344 | 9.0198 | 803.3872 | 8.9573 | 9 | 344 | 14.3333
| 345 | 8.9573 | 802.3637 | 8.895 | 8.9 | 345 | 14.375
| 346 | 8.895 | 801.3416 | 8.8327 | 8.8 | 346 | 14.4167
| 347 | 8.8327 | 800.3207 | 8.7705 | 8.8 | 347 | 14.4583
| 348 | 8.7705 | 799.3012 | 8.7083 | 8.7 | 348 | 14.5
| 349 | 8.7083 | 798.2829 | 8.6463 | 8.6 | 349 | 14.5417
| 350 | 8.6463 | 797.266 | 8.5843 | 8.6 | 350 | 14.5833
| 351 | 8.5843 | 796.2503 | 8.5224 | 8.5 | 351 | 14.625
| 352 | 8.5224 | 795.2359 | 8.4606 | 8.5 | 352 | 14.6667
| 353 | 8.4606 | 794.2229 | 8.3989 | 8.4 | 353 | 14.7083
| 354 | 8.3989 | 793.2111 | 8.3372 | 8.3 | 354 | 14.75
| 355 | 8.3372 | 792.2006 | 8.2756 | 8.3 | 355 | 14.7917
| 356 | 8.2756 | 791.1914 | 8.2141 | 8.2 | 356 | 14.8333
| 357 | 8.2141 | 790.1835 | 8.1527 | 8.2 | 357 | 14.875
| 358 | 8.1527 | 789.1768 | 8.0914 | 8.1 | 358 | 14.9167
| 359 | 8.0914 | 788.1715 | 8.0301 | 8 | 359 | 14.9583
| 360 | 8.0301 | 787.1674 | 7.9689 | 8 | 360 | 15
| 361 | 7.9689 | 786.1646 | 7.9078 | 7.9 | 361 | 15.0417
| 362 | 7.9078 | 785.1631 | 7.8468 | 7.8 | 362 | 15.0833
| 363 | 7.8468 | 784.1629 | 7.7858 | 7.8 | 363 | 15.125
| 364 | 7.7858 | 783.1639 | 7.725 | 7.7 | 364 | 15.1667
| 365 | 7.725 | 782.1662 | 7.6642 | 7.7 | 365 | 15.2083
| 366 | 7.6642 | 781.1698 | 7.6034 | 7.6 | 366 | 15.25
| 367 | 7.6034 | 780.1746 | 7.5428 | 7.5 | 367 | 15.2917
| 368 | 7.5428 | 779.1808 | 7.4822 | 7.5 | 368 | 15.3333
| 369 | 7.4822 | 778.1881 | 7.4217 | 7.4 | 369 | 15.375
| 370 | 7.4217 | 777.1968 | 7.3613 | 7.4 | 370 | 15.4167
| 371 | 7.3613 | 776.2067 | 7.301 | 7.3 | 371 | 15.4583
| 372 | 7.301 | 775.2179 | 7.2407 | 7.2 | 372 | 15.5
| 373 | 7.2407 | 774.2303 | 7.1806 | 7.2 | 373 | 15.5417
| 374 | 7.1806 | 773.244 | 7.1204 | 7.1 | 374 | 15.5833
| 375 | 7.1204 | 772.2589 | 7.0604 | 7.1 | 375 | 15.625
| 376 | 7.0604 | 771.2751 | 7.0005 | 7 | 376 | 15.6667
| 377 | 7.0005 | 770.2926 | 6.9406 | 6.9 | 377 | 15.7083
| 378 | 6.9406 | 769.3113 | 6.8808 | 6.9 | 378 | 15.75
| 379 | 6.8808 | 768.3313 | 6.8211 | 6.8 | 379 | 15.7917
| 380 | 6.8211 | 767.3525 | 6.7614 | 6.8 | 380 | 15.8333
| 381 | 6.7614 | 766.3749 | 6.7019 | 6.7 | 381 | 15.875
| 382 | 6.7019 | 765.3986 | 6.6424 | 6.6 | 382 | 15.9167
| 383 | 6.6424 | 764.4235 | 6.5829 | 6.6 | 383 | 15.9583
| 384 | 6.5829 | 763.4497 | 6.5236 | 6.5 | 384 | 16
| 385 | 6.5236 | 762.4771 | 6.4643 | 6.5 | 385 | 16.0417
| 386 | 6.4643 | 761.5058 | 6.4051 | 6.4 | 386 | 16.0833
| 387 | 6.4051 | 760.5357 | 6.346 | 6.3 | 387 | 16.125
| 388 | 6.346 | 759.5668 | 6.287 | 6.3 | 388 | 16.1667
| 389 | 6.287 | 758.5992 | 6.228 | 6.2 | 389 | 16.2083
| 390 | 6.228 | 757.6328 | 6.1691 | 6.2 | 390 | 16.25
| 391 | 6.1691 | 756.6676 | 6.1103 | 6.1 | 391 | 16.2917
| 392 | 6.1103 | 755.7037 | 6.0516 | 6.1 | 392 | 16.3333
| 393 | 6.0516 | 754.741 | 5.9929 | 6 | 393 | 16.375
| 394 | 5.9929 | 753.7795 | 5.9343 | 5.9 | 394 | 16.4167
| 395 | 5.9343 | 752.8193 | 5.8758 | 5.9 | 395 | 16.4583
| 396 | 5.8758 | 751.8602 | 5.8173 | 5.8 | 396 | 16.5
| 397 | 5.8173 | 750.9024 | 5.759 | 5.8 | 397 | 16.5417
| 398 | 5.759 | 749.9458 | 5.7007 | 5.7 | 398 | 16.5833
| 399 | 5.7007 | 748.9904 | 5.6425 | 5.6 | 399 | 16.625
| 400 | 5.6425 | 748.0363 | 5.5843 | 5.6 | 400 | 16.6667
| 401 | 5.5843 | 747.0833 | 5.5263 | 5.5 | 401 | 16.7083
| 402 | 5.5263 | 746.1316 | 5.4683 | 5.5 | 402 | 16.75
| 403 | 5.4683 | 745.1811 | 5.4103 | 5.4 | 403 | 16.7917
| 404 | 5.4103 | 744.2318 | 5.3525 | 5.4 | 404 | 16.8333
| 405 | 5.3525 | 743.2837 | 5.2947 | 5.3 | 405 | 16.875
| 406 | 5.2947 | 742.3368 | 5.237 | 5.2 | 406 | 16.9167
| 407 | 5.237 | 741.3911 | 5.1794 | 5.2 | 407 | 16.9583
| 408 | 5.1794 | 740.4467 | 5.1218 | 5.1 | 408 | 17
| 409 | 5.1218 | 739.5034 | 5.0643 | 5.1 | 409 | 17.0417
| 410 | 5.0643 | 738.5613 | 5.0069 | 5 | 410 | 17.0833
| 411 | 5.0069 | 737.6204 | 4.9496 | 4.9 | 411 | 17.125
| 412 | 4.9496 | 736.6808 | 4.8923 | 4.9 | 412 | 17.1667
| 413 | 4.8923 | 735.7423 | 4.8351 | 4.8 | 413 | 17.2083
| 414 | 4.8351 | 734.805 | 4.778 | 4.8 | 414 | 17.25
| 415 | 4.778 | 733.8689 | 4.721 | 4.7 | 415 | 17.2917
| 416 | 4.721 | 732.934 | 4.664 | 4.7 | 416 | 17.3333
| 417 | 4.664 | 732.0003 | 4.6071 | 4.6 | 417 | 17.375
| 418 | 4.6071 | 731.0678 | 4.5503 | 4.6 | 418 | 17.4167
| 419 | 4.5503 | 730.1365 | 4.4935 | 4.5 | 419 | 17.4583
| 420 | 4.4935 | 729.2064 | 4.4369 | 4.4 | 420 | 17.5
| 421 | 4.4369 | 728.2774 | 4.3802 | 4.4 | 421 | 17.5417
| 422 | 4.3802 | 727.3496 | 4.3237 | 4.3 | 422 | 17.5833
| 423 | 4.3237 | 726.423 | 4.2672 | 4.3 | 423 | 17.625
| 424 | 4.2672 | 725.4976 | 4.2108 | 4.2 | 424 | 17.6667
| 425 | 4.2108 | 724.5734 | 4.1545 | 4.2 | 425 | 17.7083
| 426 | 4.1545 | 723.6503 | 4.0983 | 4.1 | 426 | 17.75
| 427 | 4.0983 | 722.7285 | 4.0421 | 4 | 427 | 17.7917
| 428 | 4.0421 | 721.8078 | 3.986 | 4 | 428 | 17.8333
| 429 | 3.986 | 720.8882 | 3.93 | 3.9 | 429 | 17.875
| 430 | 3.93 | 719.9699 | 3.874 | 3.9 | 430 | 17.9167
| 431 | 3.874 | 719.0527 | 3.8181 | 3.8 | 431 | 17.9583
| 432 | 3.8181 | 718.1367 | 3.7623 | 3.8 | 432 | 18
| 433 | 3.7623 | 717.2218 | 3.7065 | 3.7 | 433 | 18.0417
| 434 | 3.7065 | 716.3081 | 3.6509 | 3.7 | 434 | 18.0833
| 435 | 3.6509 | 715.3956 | 3.5952 | 3.6 | 435 | 18.125 | 416887.1646
| 436 | 3.5952 | 714.4843 | 3.5397 | 3.5 | 436 | 18.1667
| 437 | 3.5397 | 713.5741 | 3.4842 | 3.5 | 437 | 18.2083
| 438 | 3.4842 | 712.665 | 3.4288 | 3.4 | 438 | 18.25
| 439 | 3.4288 | 711.7571 | 3.3735 | 3.4 | 439 | 18.2917
| 440 | 3.3735 | 710.8504 | 3.3183 | 3.3 | 440 | 18.3333
| 441 | 3.3183 | 709.9448 | 3.2631 | 3.3 | 441 | 18.375
| 442 | 3.2631 | 709.0404 | 3.208 | 3.2 | 442 | 18.4167
| 443 | 3.208 | 708.1372 | 3.1529 | 3.2 | 443 | 18.4583
| 444 | 3.1529 | 707.235 | 3.098 | 3.1 | 444 | 18.5
| 445 | 3.098 | 706.3341 | 3.043 | 3 | 445 | 18.5417
| 446 | 3.043 | 705.4343 | 2.9882 | 3 | 446 | 18.5833
| 447 | 2.9882 | 704.5356 | 2.9335 | 2.9 | 447 | 18.625
| 448 | 2.9335 | 703.6381 | 2.8788 | 2.9 | 448 | 18.6667
| 449 | 2.8788 | 702.7417 | 2.8241 | 2.8 | 449 | 18.7083
| 450 | 2.8241 | 701.8464 | 2.7696 | 2.8 | 450 | 18.75
| 451 | 2.7696 | 700.9524 | 2.7151 | 2.7 | 451 | 18.7917
| 452 | 2.7151 | 700.0594 | 2.6607 | 2.7 | 452 | 18.8333
| 453 | 2.6607 | 699.1676 | 2.6063 | 2.6 | 453 | 18.875
| 454 | 2.6063 | 698.2769 | 2.5521 | 2.6 | 454 | 18.9167
| 455 | 2.5521 | 697.3873 | 2.4978 | 2.5 | 455 | 18.9583
| 456 | 2.4978 | 696.4989 | 2.4437 | 2.4 | 456 | 19
| 457 | 2.4437 | 695.6116 | 2.3896 | 2.4 | 457 | 19.0417
| 458 | 2.3896 | 694.7255 | 2.3356 | 2.3 | 458 | 19.0833
| 459 | 2.3356 | 693.8404 | 2.2817 | 2.3 | 459 | 19.125
| 460 | 2.2817 | 692.9565 | 2.2278 | 2.2 | 460 | 19.1667
| 461 | 2.2278 | 692.0738 | 2.174 | 2.2 | 461 | 19.2083
| 462 | 2.174 | 691.1921 | 2.1203 | 2.1 | 462 | 19.25
| 463 | 2.1203 | 690.3116 | 2.0667 | 2.1 | 463 | 19.2917
| 464 | 2.0667 | 689.4322 | 2.0131 | 2 | 464 | 19.3333
| 465 | 2.0131 | 688.5539 | 1.9595 | 2 | 465 | 19.375
| 466 | 1.9595 | 687.6767 | 1.9061 | 1.9 | 466 | 19.4167
| 467 | 1.9061 | 686.8007 | 1.8527 | 1.9 | 467 | 19.4583
| 468 | 1.8527 | 685.9257 | 1.7994 | 1.8 | 468 | 19.5
| 469 | 1.7994 | 685.0519 | 1.7461 | 1.7 | 469 | 19.5417
| 470 | 1.7461 | 684.1792 | 1.693 | 1.7 | 470 | 19.5833
| 471 | 1.693 | 683.3076 | 1.6398 | 1.6 | 471 | 19.625
| 472 | 1.6398 | 682.4372 | 1.5868 | 1.6 | 472 | 19.6667
| 473 | 1.5868 | 681.5678 | 1.5338 | 1.5 | 473 | 19.7083
| 474 | 1.5338 | 680.6995 | 1.4809 | 1.5 | 474 | 19.75
| 475 | 1.4809 | 679.8324 | 1.4281 | 1.4 | 475 | 19.7917
| 476 | 1.4281 | 678.9663 | 1.3753 | 1.4 | 476 | 19.8333
| 477 | 1.3753 | 678.1013 | 1.3226 | 1.3 | 477 | 19.875
| 478 | 1.3226 | 677.2375 | 1.2699 | 1.3 | 478 | 19.9167
| 479 | 1.2699 | 676.3747 | 1.2174 | 1.2 | 479 | 19.9583
| 480 | 1.2174 | 675.5131 | 1.1649 | 1.2 | 480 | 20
| 481 | 1.1649 | 674.6525 | 1.1124 | 1.1 | 481 | 20.0417
| 482 | 1.1124 | 673.7931 | 1.06 | 1.1 | 482 | 20.0833
| 483 | 1.06 | 672.9347 | 1.0077 | 1 | 483 | 20.125
| 484 | 1.0077 | 672.0775 | 0.9555 | 1 | 484 | 20.1667
| 485 | 0.9555 | 671.2213 | 0.90332 | 0.9 | 485 | 20.2083
| 486 | 0.90332 | 670.3662 | 0.85121 | 0.9 | 486 | 20.25
| 487 | 0.85121 | 669.5122 | 0.79917 | 0.8 | 487 | 20.2917
| 488 | 0.79917 | 668.6593 | 0.7472 | 0.7 | 488 | 20.3333
| 489 | 0.7472 | 667.8075 | 0.69529 | 0.7 | 489 | 20.375
| 490 | 0.69529 | 666.9567 | 0.64345 | 0.6 | 490 | 20.4167
| 491 | 0.64345 | 666.1071 | 0.59167 | 0.6 | 491 | 20.4583
| 492 | 0.59167 | 665.2585 | 0.53996 | 0.5 | 492 | 20.5
| 493 | 0.53996 | 664.411 | 0.48831 | 0.5 | 493 | 20.5417
| 494 | 0.48831 | 663.5646 | 0.43673 | 0.4 | 494 | 20.5833
| 495 | 0.43673 | 662.7193 | 0.38522 | 0.4 | 495 | 20.625
| 496 | 0.38522 | 661.875 | 0.33377 | 0.3 | 496 | 20.6667
| 497 | 0.33377 | 661.0318 | 0.28239 | 0.3 | 497 | 20.7083
| 498 | 0.28239 | 660.1897 | 0.23107 | 0.2 | 498 | 20.75
| 499 | 0.23107 | 659.3487 | 0.17982 | 0.2 | 499 | 20.7917
| 500 | 0.17982 | 658.5087 | 0.12864 | 0.1 | 500 | 20.8333
| 501 | 0.12864 | 657.6699 | 0.077516 | 0.1 | 501 | 20.875
| 502 | 0.077516 | 656.832 | 0.02646 | 0 | 502 | 20.9167
| 503 | 0.02646 | 655.9953 | -0.024531 | 0 | 503 | 20.9583
| 504 | -0.024531 | 655.1596 | -0.075456 | -0.1 | 504 | 21
| 505 | -0.075456 | 654.325 | -0.12632 | -0.1 | 505 | 21.0417
| 506 | -0.12632 | 653.4914 | -0.17711 | -0.2 | 506 | 21.0833
| 507 | -0.17711 | 652.6589 | -0.22784 | -0.2 | 507 | 21.125
| 508 | -0.22784 | 651.8275 | -0.27851 | -0.3 | 508 | 21.1667
| 509 | -0.27851 | 650.9971 | -0.32911 | -0.3 | 509 | 21.2083
| 510 | -0.32911 | 650.1678 | -0.37965 | -0.4 | 510 | 21.25
| 511 | -0.37965 | 649.3395 | -0.43012 | -0.4 | 511 | 21.2917
| 512 | -0.43012 | 648.5123 | -0.48053 | -0.5 | 512 | 21.3333
| 513 | -0.48053 | 647.6861 | -0.53088 | -0.5 | 513 | 21.375
| 514 | -0.53088 | 646.861 | -0.58116 | -0.6 | 514 | 21.4167
| 515 | -0.58116 | 646.037 | -0.63138 | -0.6 | 515 | 21.4583
| 516 | -0.63138 | 645.214 | -0.68153 | -0.7 | 516 | 21.5
| 517 | -0.68153 | 644.392 | -0.73162 | -0.7 | 517 | 21.5417
| 518 | -0.73162 | 643.5711 | -0.78164 | -0.8 | 518 | 21.5833
| 519 | -0.78164 | 642.7513 | -0.8316 | -0.8 | 519 | 21.625
| 520 | -0.8316 | 641.9324 | -0.8815 | -0.9 | 520 | 21.6667
| 521 | -0.8815 | 641.1147 | -0.93134 | -0.9 | 521 | 21.7083
| 522 | -0.93134 | 640.2979 | -0.98111 | -1 | 522 | 21.75
| 523 | -0.98111 | 639.4822 | -1.0308 | -1 | 523 | 21.7917
| 524 | -1.0308 | 638.6676 | -1.0805 | -1.1 | 524 | 21.8333
| 525 | -1.0805 | 637.854 | -1.13 | -1.1 | 525 | 21.875
| 526 | -1.13 | 637.0414 | -1.1796 | -1.2 | 526 | 21.9167
| 527 | -1.1796 | 636.2299 | -1.229 | -1.2 | 527 | 21.9583
| 528 | -1.229 | 635.4194 | -1.2784 | -1.3 | 528 | 22
| 529 | -1.2784 | 634.6099 | -1.3277 | -1.3 | 529 | 22.0417
| 530 | -1.3277 | 633.8014 | -1.377 | -1.4 | 530 | 22.0833
| 531 | -1.377 | 632.994 | -1.4262 | -1.4 | 531 | 22.125
| 532 | -1.4262 | 632.1876 | -1.4753 | -1.5 | 532 | 22.1667
| 533 | -1.4753 | 631.3823 | -1.5244 | -1.5 | 533 | 22.2083
| 534 | -1.5244 | 630.5779 | -1.5734 | -1.6 | 534 | 22.25
| 535 | -1.5734 | 629.7746 | -1.6224 | -1.6 | 535 | 22.2917
| 536 | -1.6224 | 628.9723 | -1.6713 | -1.7 | 536 | 22.3333
| 537 | -1.6713 | 628.1711 | -1.7201 | -1.7 | 537 | 22.375
| 538 | -1.7201 | 627.3708 | -1.7689 | -1.8 | 538 | 22.4167
| 539 | -1.7689 | 626.5716 | -1.8176 | -1.8 | 539 | 22.4583
| 540 | -1.8176 | 625.7734 | -1.8662 | -1.9 | 540 | 22.5
| 541 | -1.8662 | 624.9762 | -1.9148 | -1.9 | 541 | 22.5417
| 542 | -1.9148 | 624.18 | -1.9633 | -2 | 542 | 22.5833
| 543 | -1.9633 | 623.3849 | -2.0118 | -2 | 543 | 22.625
| 544 | -2.0118 | 622.5907 | -2.0602 | -2.1 | 544 | 22.6667
| 545 | -2.0602 | 621.7976 | -2.1085 | -2.1 | 545 | 22.7083
| 546 | -2.1085 | 621.0055 | -2.1568 | -2.2 | 546 | 22.75
| 547 | -2.1568 | 620.2144 | -2.205 | -2.2 | 547 | 22.7917
| 548 | -2.205 | 619.4243 | -2.2531 | -2.3 | 548 | 22.8333
| 549 | -2.2531 | 618.6352 | -2.3012 | -2.3 | 549 | 22.875
| 550 | -2.3012 | 617.8471 | -2.3492 | -2.3 | 550 | 22.9167
| 551 | -2.3492 | 617.06 | -2.3972 | -2.4 | 551 | 22.9583
| 552 | -2.3972 | 616.2739 | -2.4451 | -2.4 | 552 | 23
| 553 | -2.4451 | 615.4888 | -2.4929 | -2.5 | 553 | 23.0417
| 554 | -2.4929 | 614.7047 | -2.5407 | -2.5 | 554 | 23.0833
| 555 | -2.5407 | 613.9216 | -2.5884 | -2.6 | 555 | 23.125
| 556 | -2.5884 | 613.1395 | -2.6361 | -2.6 | 556 | 23.1667
| 557 | -2.6361 | 612.3584 | -2.6837 | -2.7 | 557 | 23.2083
| 558 | -2.6837 | 611.5784 | -2.7312 | -2.7 | 558 | 23.25
| 559 | -2.7312 | 610.7992 | -2.7787 | -2.8 | 559 | 23.2917
| 560 | -2.7787 | 610.0211 | -2.8261 | -2.8 | 560 | 23.3333
| 561 | -2.8261 | 609.244 | -2.8735 | -2.9 | 561 | 23.375
| 562 | -2.8735 | 608.4679 | -2.9208 | -2.9 | 562 | 23.4167
| 563 | -2.9208 | 607.6927 | -2.968 | -3 | 563 | 23.4583
| 564 | -2.968 | 606.9186 | -3.0152 | -3 | 564 | 23.5
| 565 | -3.0152 | 606.1454 | -3.0623 | -3.1 | 565 | 23.5417
| 566 | -3.0623 | 605.3732 | -3.1094 | -3.1 | 566 | 23.5833
| 567 | -3.1094 | 604.602 | -3.1564 | -3.2 | 567 | 23.625
| 568 | -3.1564 | 603.8318 | -3.2033 | -3.2 | 568 | 23.6667
| 569 | -3.2033 | 603.0626 | -3.2502 | -3.3 | 569 | 23.7083
| 570 | -3.2502 | 602.2943 | -3.297 | -3.3 | 570 | 23.75
| 571 | -3.297 | 601.527 | -3.3438 | -3.3 | 571 | 23.7917
| 572 | -3.3438 | 600.7607 | -3.3904 | -3.4 | 572 | 23.8333
| 573 | -3.3904 | 599.9954 | -3.4371 | -3.4 | 573 | 23.875
| 574 | -3.4371 | 599.2311 | -3.4837 | -3.5 | 574 | 23.9167
| 575 | -3.4837 | 598.4677 | -3.5302 | -3.5 | 575 | 23.9583
| 576 | -3.5302 | 597.7053 | -3.5766 | -3.6 | 576 | 24
| 577 | -3.5766 | 596.9439 | -3.623 | -3.6 | 577 | 24.0417
| 578 | -3.623 | 596.1834 | -3.6694 | -3.7 | 578 | 24.0833
| 579 | -3.6694 | 595.4239 | -3.7157 | -3.7 | 579 | 24.125
| 580 | -3.7157 | 594.6654 | -3.7619 | -3.8 | 580 | 24.1667
| 581 | -3.7619 | 593.9078 | -3.8081 | -3.8 | 581 | 24.2083
| 582 | -3.8081 | 593.1512 | -3.8542 | -3.9 | 582 | 24.25
| 583 | -3.8542 | 592.3956 | -3.9002 | -3.9 | 583 | 24.2917
| 584 | -3.9002 | 591.6409 | -3.9462 | -3.9 | 584 | 24.3333
| 585 | -3.9462 | 590.8872 | -3.9921 | -4 | 585 | 24.375
| 586 | -3.9921 | 590.1345 | -4.038 | -4 | 586 | 24.4167
| 587 | -4.038 | 589.3827 | -4.0838 | -4.1 | 587 | 24.4583
| 588 | -4.0838 | 588.6319 | -4.1296 | -4.1 | 588 | 24.5
| 589 | -4.1296 | 587.882 | -4.1753 | -4.2 | 589 | 24.5417
| 590 | -4.1753 | 587.1331 | -4.2209 | -4.2 | 590 | 24.5833
| 591 | -4.2209 | 586.3851 | -4.2665 | -4.3 | 591 | 24.625
| 592 | -4.2665 | 585.6381 | -4.312 | -4.3 | 592 | 24.6667
| 593 | -4.312 | 584.892 | -4.3575 | -4.4 | 593 | 24.7083
| 594 | -4.3575 | 584.1469 | -4.4029 | -4.4 | 594 | 24.75
| 595 | -4.4029 | 583.4028 | -4.4482 | -4.4 | 595 | 24.7917
| 596 | -4.4482 | 582.6596 | -4.4935 | -4.5 | 596 | 24.8333
| 597 | -4.4935 | 581.9173 | -4.5387 | -4.5 | 597 | 24.875
| 598 | -4.5387 | 581.176 | -4.5839 | -4.6 | 598 | 24.9167
| 599 | -4.5839 | 580.4356 | -4.629 | -4.6 | 599 | 24.9583
| 600 | -4.629 | 579.6962 | -4.6741 | -4.7 | 600 | 25
| 601 | -4.6741 | 578.9577 | -4.7191 | -4.7 | 601 | 25.0417
| 602 | -4.7191 | 578.2201 | -4.764 | -4.8 | 602 | 25.0833
| 603 | -4.764 | 577.4835 | -4.8089 | -4.8 | 603 | 25.125
| 604 | -4.8089 | 576.7479 | -4.8538 | -4.9 | 604 | 25.1667
| 605 | -4.8538 | 576.0131 | -4.8985 | -4.9 | 605 | 25.2083
| 606 | -4.8985 | 575.2793 | -4.9433 | -4.9 | 606 | 25.25
| 607 | -4.9433 | 574.5465 | -4.9879 | -5 | 607 | 25.2917
| 608 | -4.9879 | 573.8145 | -5.0325 | -5 | 608 | 25.3333
| 609 | -5.0325 | 573.0835 | -5.0771 | -5.1 | 609 | 25.375
| 610 | -5.0771 | 572.3535 | -5.1215 | -5.1 | 610 | 25.4167
| 611 | -5.1215 | 571.6243 | -5.166 | -5.2 | 611 | 25.4583
| 612 | -5.166 | 570.8961 | -5.2104 | -5.2 | 612 | 25.5
| 613 | -5.2104 | 570.1689 | -5.2547 | -5.3 | 613 | 25.5417
| 614 | -5.2547 | 569.4425 | -5.2989 | -5.3 | 614 | 25.5833
| 615 | -5.2989 | 568.7171 | -5.3431 | -5.3 | 615 | 25.625
| 616 | -5.3431 | 567.9926 | -5.3873 | -5.4 | 616 | 25.6667
| 617 | -5.3873 | 567.269 | -5.4314 | -5.4 | 617 | 25.7083
| 618 | -5.4314 | 566.5463 | -5.4754 | -5.5 | 618 | 25.75
| 619 | -5.4754 | 565.8246 | -5.5194 | -5.5 | 619 | 25.7917
| 620 | -5.5194 | 565.1038 | -5.5633 | -5.6 | 620 | 25.8333
| 621 | -5.5633 | 564.3839 | -5.6072 | -5.6 | 621 | 25.875
| 622 | -5.6072 | 563.6649 | -5.651 | -5.7 | 622 | 25.9167
| 623 | -5.651 | 562.9468 | -5.6948 | -5.7 | 623 | 25.9583
| 624 | -5.6948 | 562.2297 | -5.7385 | -5.7 | 624 | 26
| 625 | -5.7385 | 561.5134 | -5.7821 | -5.8 | 625 | 26.0417
| 626 | -5.7821 | 560.7981 | -5.8257 | -5.8 | 626 | 26.0833
| 627 | -5.8257 | 560.0837 | -5.8693 | -5.9 | 627 | 26.125
| 628 | -5.8693 | 559.3702 | -5.9127 | -5.9 | 628 | 26.1667
| 629 | -5.9127 | 558.6576 | -5.9562 | -6 | 629 | 26.2083
| 630 | -5.9562 | 557.9459 | -5.9995 | -6 | 630 | 26.25
| 631 | -5.9995 | 557.2351 | -6.0428 | -6 | 631 | 26.2917
| 632 | -6.0428 | 556.5253 | -6.0861 | -6.1 | 632 | 26.3333
| 633 | -6.0861 | 555.8163 | -6.1293 | -6.1 | 633 | 26.375
| 634 | -6.1293 | 555.1082 | -6.1725 | -6.2 | 634 | 26.4167
| 635 | -6.1725 | 554.401 | -6.2155 | -6.2 | 635 | 26.4583
| 636 | -6.2155 | 553.6948 | -6.2586 | -6.3 | 636 | 26.5
| 637 | -6.2586 | 552.9894 | -6.3016 | -6.3 | 637 | 26.5417
| 638 | -6.3016 | 552.285 | -6.3445 | -6.3 | 638 | 26.5833
| 639 | -6.3445 | 551.5814 | -6.3874 | -6.4 | 639 | 26.625
| 640 | -6.3874 | 550.8787 | -6.4302 | -6.4 | 640 | 26.6667
| 641 | -6.4302 | 550.1769 | -6.473 | -6.5 | 641 | 26.7083
| 642 | -6.473 | 549.476 | -6.5157 | -6.5 | 642 | 26.75
| 643 | -6.5157 | 548.7761 | -6.5583 | -6.6 | 643 | 26.7917
| 644 | -6.5583 | 548.077 | -6.6009 | -6.6 | 644 | 26.8333
| 645 | -6.6009 | 547.3787 | -6.6435 | -6.6 | 645 | 26.875
| 646 | -6.6435 | 546.6814 | -6.686 | -6.7 | 646 | 26.9167
| 647 | -6.686 | 545.985 | -6.7284 | -6.7 | 647 | 26.9583
| 648 | -6.7284 | 545.2895 | -6.7708 | -6.8 | 648 | 27
| 649 | -6.7708 | 544.5948 | -6.8131 | -6.8 | 649 | 27.0417
| 650 | -6.8131 | 543.901 | -6.8554 | -6.9 | 650 | 27.0833
| 651 | -6.8554 | 543.2081 | -6.8976 | -6.9 | 651 | 27.125
| 652 | -6.8976 | 542.5161 | -6.9398 | -6.9 | 652 | 27.1667
| 653 | -6.9398 | 541.825 | -6.9819 | -7 | 653 | 27.2083
| 654 | -6.9819 | 541.1348 | -7.024 | -7 | 654 | 27.25
| 655 | -7.024 | 540.4454 | -7.066 | -7.1 | 655 | 27.2917
| 656 | -7.066 | 539.7569 | -7.1079 | -7.1 | 656 | 27.3333
| 657 | -7.1079 | 539.0693 | -7.1498 | -7.1 | 657 | 27.375
| 658 | -7.1498 | 538.3826 | -7.1917 | -7.2 | 658 | 27.4167
| 659 | -7.1917 | 537.6967 | -7.2335 | -7.2 | 659 | 27.4583
| 660 | -7.2335 | 537.0117 | -7.2752 | -7.3 | 660 | 27.5
| 661 | -7.2752 | 536.3276 | -7.3169 | -7.3 | 661 | 27.5417
| 662 | -7.3169 | 535.6444 | -7.3586 | -7.4 | 662 | 27.5833
| 663 | -7.3586 | 534.962 | -7.4001 | -7.4 | 663 | 27.625
| 664 | -7.4001 | 534.2805 | -7.4417 | -7.4 | 664 | 27.6667
| 665 | -7.4417 | 533.5999 | -7.4831 | -7.5 | 665 | 27.7083
| 666 | -7.4831 | 532.9201 | -7.5246 | -7.5 | 666 | 27.75
| 667 | -7.5246 | 532.2412 | -7.5659 | -7.6 | 667 | 27.7917
| 668 | -7.5659 | 531.5632 | -7.6073 | -7.6 | 668 | 27.8333
| 669 | -7.6073 | 530.886 | -7.6485 | -7.6 | 669 | 27.875
| 670 | -7.6485 | 530.2097 | -7.6897 | -7.7 | 670 | 27.9167
| 671 | -7.6897 | 529.5342 | -7.7309 | -7.7 | 671 | 27.9583
| 672 | -7.7309 | 528.8596 | -7.772 | -7.8 | 672 | 28
| 673 | -7.772 | 528.1859 | -7.8131 | -7.8 | 673 | 28.0417
| 674 | -7.8131 | 527.5131 | -7.8541 | -7.9 | 674 | 28.0833
| 675 | -7.8541 | 526.841 | -7.895 | -7.9 | 675 | 28.125
| 676 | -7.895 | 526.1699 | -7.9359 | -7.9 | 676 | 28.1667
| 677 | -7.9359 | 525.4996 | -7.9768 | -8 | 677 | 28.2083
| 678 | -7.9768 | 524.8301 | -8.0176 | -8 | 678 | 28.25
| 679 | -8.0176 | 524.1615 | -8.0583 | -8.1 | 679 | 28.2917
| 680 | -8.0583 | 523.4938 | -8.099 | -8.1 | 680 | 28.3333
| 681 | -8.099 | 522.8269 | -8.1396 | -8.1 | 681 | 28.375
| 682 | -8.1396 | 522.1609 | -8.1802 | -8.2 | 682 | 28.4167
| 683 | -8.1802 | 521.4957 | -8.2208 | -8.2 | 683 | 28.4583
| 684 | -8.2208 | 520.8313 | -8.2612 | -8.3 | 684 | 28.5
| 685 | -8.2612 | 520.1678 | -8.3017 | -8.3 | 685 | 28.5417
| 686 | -8.3017 | 519.5052 | -8.3421 | -8.3 | 686 | 28.5833
| 687 | -8.3421 | 518.8434 | -8.3824 | -8.4 | 687 | 28.625
| 688 | -8.3824 | 518.1824 | -8.4227 | -8.4 | 688 | 28.6667
| 689 | -8.4227 | 517.5223 | -8.4629 | -8.5 | 689 | 28.7083
| 690 | -8.4629 | 516.863 | -8.5031 | -8.5 | 690 | 28.75
| 691 | -8.5031 | 516.2045 | -8.5432 | -8.5 | 691 | 28.7917
| 692 | -8.5432 | 515.5469 | -8.5833 | -8.6 | 692 | 28.8333
| 693 | -8.5833 | 514.8902 | -8.6233 | -8.6 | 693 | 28.875
| 694 | -8.6233 | 514.2342 | -8.6633 | -8.7 | 694 | 28.9167
| 695 | -8.6633 | 513.5791 | -8.7032 | -8.7 | 695 | 28.9583
| 696 | -8.7032 | 512.9249 | -8.743 | -8.7 | 696 | 29
| 697 | -8.743 | 512.2715 | -8.7829 | -8.8 | 697 | 29.0417
| 698 | -8.7829 | 511.6189 | -8.8226 | -8.8 | 698 | 29.0833
| 699 | -8.8226 | 510.9671 | -8.8624 | -8.9 | 699 | 29.125
| 700 | -8.8624 | 510.3162 | -8.902 | -8.9 | 700 | 29.1667
| 701 | -8.902 | 509.6661 | -8.9416 | -8.9 | 701 | 29.2083
| 702 | -8.9416 | 509.0168 | -8.9812 | -9 | 702 | 29.25
| 703 | -8.9812 | 508.3683 | -9.0207 | -9 | 703 | 29.2917
| 704 | -9.0207 | 507.7207 | -9.0602 | -9.1 | 704 | 29.3333
| 705 | -9.0602 | 507.0739 | -9.0996 | -9.1 | 705 | 29.375
| 706 | -9.0996 | 506.4279 | -9.139 | -9.1 | 706 | 29.4167
| 707 | -9.139 | 505.7828 | -9.1783 | -9.2 | 707 | 29.4583
| 708 | -9.1783 | 505.1385 | -9.2175 | -9.2 | 708 | 29.5
| 709 | -9.2175 | 504.4949 | -9.2568 | -9.3 | 709 | 29.5417
| 710 | -9.2568 | 503.8523 | -9.2959 | -9.3 | 710 | 29.5833
| 711 | -9.2959 | 503.2104 | -9.335 | -9.3 | 711 | 29.625
| 712 | -9.335 | 502.5693 | -9.3741 | -9.4 | 712 | 29.6667
| 713 | -9.3741 | 501.9291 | -9.4131 | -9.4 | 713 | 29.7083
| 714 | -9.4131 | 501.2897 | -9.4521 | -9.5 | 714 | 29.75
| 715 | -9.4521 | 500.6511 | -9.491 | -9.5 | 715 | 29.7917
| 716 | -9.491 | 500.0133 | -9.5299 | -9.5 | 716 | 29.8333
| 717 | -9.5299 | 499.3763 | -9.5687 | -9.6 | 717 | 29.875
| 718 | -9.5687 | 498.7401 | -9.6074 | -9.6 | 718 | 29.9167
| 719 | -9.6074 | 498.1048 | -9.6462 | -9.6 | 719 | 29.9583
| 720 | -9.6462 | 497.4702 | -9.6848 | -9.7 | 720 | 30
| 721 | -9.6848 | 496.8365 | -9.7235 | -9.7 | 721 | 30.0417
| 722 | -9.7235 | 496.2036 | -9.762 | -9.8 | 722 | 30.0833
| 723 | -9.762 | 495.5714 | -9.8005 | -9.8 | 723 | 30.125
| 724 | -9.8005 | 494.9401 | -9.839 | -9.8 | 724 | 30.1667
| 725 | -9.839 | 494.3096 | -9.8774 | -9.9 | 725 | 30.2083
| 726 | -9.8774 | 493.6799 | -9.9158 | -9.9 | 726 | 30.25
| 727 | -9.9158 | 493.051 | -9.9541 | -10 | 727 | 30.2917
| 728 | -9.9541 | 492.4229 | -9.9924 | -10 | 728 | 30.3333
| 729 | -9.9924 | 491.7956 | -10.0306 | -10 | 729 | 30.375
| 730 | -10.0306 | 491.169 | -10.0688 | -10.1 | 730 | 30.4167
| 731 | -10.0688 | 490.5433 | -10.107 | -10.1 | 731 | 30.4583
| 732 | -10.107 | 489.9184 | -10.145 | -10.1 | 732 | 30.5
| 733 | -10.145 | 489.2943 | -10.1831 | -10.2 | 733 | 30.5417
| 734 | -10.1831 | 488.671 | -10.221 | -10.2 | 734 | 30.5833
| 735 | -10.221 | 488.0484 | -10.259 | -10.3 | 735 | 30.625
| 736 | -10.259 | 487.4267 | -10.2969 | -10.3 | 736 | 30.6667
| 737 | -10.2969 | 486.8058 | -10.3347 | -10.3 | 737 | 30.7083
| 738 | -10.3347 | 486.1856 | -10.3725 | -10.4 | 738 | 30.75
| 739 | -10.3725 | 485.5662 | -10.4102 | -10.4 | 739 | 30.7917
| 740 | -10.4102 | 484.9477 | -10.4479 | -10.4 | 740 | 30.8333
| 741 | -10.4479 | 484.3299 | -10.4856 | -10.5 | 741 | 30.875
| 742 | -10.4856 | 483.7129 | -10.5232 | -10.5 | 742 | 30.9167
| 743 | -10.5232 | 483.0967 | -10.5607 | -10.6 | 743 | 30.9583
| 744 | -10.5607 | 482.4812 | -10.5982 | -10.6 | 744 | 31
| 745 | -10.5982 | 481.8666 | -10.6357 | -10.6 | 745 | 31.0417
| 746 | -10.6357 | 481.2527 | -10.6731 | -10.7 | 746 | 31.0833
| 747 | -10.6731 | 480.6397 | -10.7105 | -10.7 | 747 | 31.125
| 748 | -10.7105 | 480.0274 | -10.7478 | -10.7 | 748 | 31.1667
| 749 | -10.7478 | 479.4158 | -10.785 | -10.8 | 749 | 31.2083
| 750 | -10.785 | 478.8051 | -10.8223 | -10.8 | 750 | 31.25
| 751 | -10.8223 | 478.1951 | -10.8594 | -10.9 | 751 | 31.2917
| 752 | -10.8594 | 477.5859 | -10.8966 | -10.9 | 752 | 31.3333
| 753 | -10.8966 | 476.9775 | -10.9336 | -10.9 | 753 | 31.375
| 754 | -10.9336 | 476.3699 | -10.9707 | -11 | 754 | 31.4167
| 755 | -10.9707 | 475.763 | -11.0076 | -11 | 755 | 31.4583
| 756 | -11.0076 | 475.157 | -11.0446 | -11 | 756 | 31.5
| 757 | -11.0446 | 474.5516 | -11.0815 | -11.1 | 757 | 31.5417
| 758 | -11.0815 | 473.9471 | -11.1183 | -11.1 | 758 | 31.5833
| 759 | -11.1183 | 473.3433 | -11.1551 | -11.2 | 759 | 31.625
| 760 | -11.1551 | 472.7403 | -11.1918 | -11.2 | 760 | 31.6667
| 761 | -11.1918 | 472.1381 | -11.2285 | -11.2 | 761 | 31.7083
| 762 | -11.2285 | 471.5366 | -11.2652 | -11.3 | 762 | 31.75
| 763 | -11.2652 | 470.9359 | -11.3018 | -11.3 | 763 | 31.7917
| 764 | -11.3018 | 470.336 | -11.3384 | -11.3 | 764 | 31.8333
| 765 | -11.3384 | 469.7368 | -11.3749 | -11.4 | 765 | 31.875
| 766 | -11.3749 | 469.1384 | -11.4113 | -11.4 | 766 | 31.9167
| 767 | -11.4113 | 468.5408 | -11.4478 | -11.4 | 767 | 31.9583
| 768 | -11.4478 | 467.9439 | -11.4841 | -11.5 | 768 | 32
| 769 | -11.4841 | 467.3477 | -11.5205 | -11.5 | 769 | 32.0417
| 770 | -11.5205 | 466.7524 | -11.5567 | -11.6 | 770 | 32.0833
| 771 | -11.5567 | 466.1578 | -11.593 | -11.6 | 771 | 32.125
| 772 | -11.593 | 465.5639 | -11.6292 | -11.6 | 772 | 32.1667
| 773 | -11.6292 | 464.9708 | -11.6653 | -11.7 | 773 | 32.2083
| 774 | -11.6653 | 464.3785 | -11.7014 | -11.7 | 774 | 32.25
| 775 | -11.7014 | 463.7869 | -11.7375 | -11.7 | 775 | 32.2917
| 776 | -11.7375 | 463.1961 | -11.7735 | -11.8 | 776 | 32.3333
| 777 | -11.7735 | 462.606 | -11.8094 | -11.8 | 777 | 32.375
| 778 | -11.8094 | 462.0167 | -11.8453 | -11.8 | 778 | 32.4167
| 779 | -11.8453 | 461.4281 | -11.8812 | -11.9 | 779 | 32.4583
| 780 | -11.8812 | 460.8403 | -11.917 | -11.9 | 780 | 32.5
| 781 | -11.917 | 460.2532 | -11.9528 | -12 | 781 | 32.5417
| 782 | -11.9528 | 459.6669 | -11.9885 | -12 | 782 | 32.5833
| 783 | -11.9885 | 459.0813 | -12.0242 | -12 | 783 | 32.625
| 784 | -12.0242 | 458.4965 | -12.0598 | -12.1 | 784 | 32.6667
| 785 | -12.0598 | 457.9124 | -12.0954 | -12.1 | 785 | 32.7083
| 786 | -12.0954 | 457.329 | -12.131 | -12.1 | 786 | 32.75
| 787 | -12.131 | 456.7464 | -12.1665 | -12.2 | 787 | 32.7917
| 788 | -12.1665 | 456.1646 | -12.2019 | -12.2 | 788 | 32.8333
| 789 | -12.2019 | 455.5834 | -12.2374 | -12.2 | 789 | 32.875
| 790 | -12.2374 | 455.0031 | -12.2727 | -12.3 | 790 | 32.9167
| 791 | -12.2727 | 454.4234 | -12.308 | -12.3 | 791 | 32.9583
| 792 | -12.308 | 453.8445 | -12.3433 | -12.3 | 792 | 33
| 793 | -12.3433 | 453.2664 | -12.3786 | -12.4 | 793 | 33.0417
| 794 | -12.3786 | 452.6889 | -12.4137 | -12.4 | 794 | 33.0833
| 795 | -12.4137 | 452.1122 | -12.4489 | -12.4 | 795 | 33.125
| 796 | -12.4489 | 451.5363 | -12.484 | -12.5 | 796 | 33.1667
| 797 | -12.484 | 450.9611 | -12.519 | -12.5 | 797 | 33.2083
| 798 | -12.519 | 450.3866 | -12.554 | -12.6 | 798 | 33.25
| 799 | -12.554 | 449.8128 | -12.589 | -12.6 | 799 | 33.2917
| 800 | -12.589 | 449.2398 | -12.6239 | -12.6 | 800 | 33.3333
| 801 | -12.6239 | 448.6675 | -12.6588 | -12.7 | 801 | 33.375
| 802 | -12.6588 | 448.0959 | -12.6936 | -12.7 | 802 | 33.4167
| 803 | -12.6936 | 447.5251 | -12.7284 | -12.7 | 803 | 33.4583
| 804 | -12.7284 | 446.955 | -12.7632 | -12.8 | 804 | 33.5
| 805 | -12.7632 | 446.3856 | -12.7979 | -12.8 | 805 | 33.5417
| 806 | -12.7979 | 445.8169 | -12.8325 | -12.8 | 806 | 33.5833
| 807 | -12.8325 | 445.249 | -12.8671 | -12.9 | 807 | 33.625
| 808 | -12.8671 | 444.6818 | -12.9017 | -12.9 | 808 | 33.6667
| 809 | -12.9017 | 444.1153 | -12.9362 | -12.9 | 809 | 33.7083
| 810 | -12.9362 | 443.5495 | -12.9707 | -13 | 810 | 33.75
| 811 | -12.9707 | 442.9844 | -13.0051 | -13 | 811 | 33.7917
| 812 | -13.0051 | 442.4201 | -13.0395 | -13 | 812 | 33.8333
| 813 | -13.0395 | 441.8565 | -13.0739 | -13.1 | 813 | 33.875
| 814 | -13.0739 | 441.2936 | -13.1082 | -13.1 | 814 | 33.9167
| 815 | -13.1082 | 440.7314 | -13.1424 | -13.1 | 815 | 33.9583
| 816 | -13.1424 | 440.17 | -13.1766 | -13.2 | 816 | 34
| 817 | -13.1766 | 439.6092 | -13.2108 | -13.2 | 817 | 34.0417
| 818 | -13.2108 | 439.0492 | -13.2449 | -13.2 | 818 | 34.0833
| 819 | -13.2449 | 438.4899 | -13.279 | -13.3 | 819 | 34.125
| 820 | -13.279 | 437.9313 | -13.3131 | -13.3 | 820 | 34.1667
| 821 | -13.3131 | 437.3734 | -13.3471 | -13.3 | 821 | 34.2083
| 822 | -13.3471 | 436.8162 | -13.381 | -13.4 | 822 | 34.25
| 823 | -13.381 | 436.2598 | -13.4149 | -13.4 | 823 | 34.2917
| 824 | -13.4149 | 435.704 | -13.4488 | -13.4 | 824 | 34.3333
| 825 | -13.4488 | 435.1489 | -13.4826 | -13.5 | 825 | 34.375
| 826 | -13.4826 | 434.5946 | -13.5164 | -13.5 | 826 | 34.4167
| 827 | -13.5164 | 434.0409 | -13.5501 | -13.6 | 827 | 34.4583
| 828 | -13.5501 | 433.488 | -13.5838 | -13.6 | 828 | 34.5
| 829 | -13.5838 | 432.9358 | -13.6175 | -13.6 | 829 | 34.5417
| 830 | -13.6175 | 432.3843 | -13.6511 | -13.7 | 830 | 34.5833
| 831 | -13.6511 | 431.8334 | -13.6847 | -13.7 | 831 | 34.625
| 832 | -13.6847 | 431.2833 | -13.7182 | -13.7 | 832 | 34.6667
| 833 | -13.7182 | 430.7339 | -13.7517 | -13.8 | 833 | 34.7083
| 834 | -13.7517 | 430.1852 | -13.7851 | -13.8 | 834 | 34.75
| 835 | -13.7851 | 429.6371 | -13.8185 | -13.8 | 835 | 34.7917
| 836 | -13.8185 | 429.0898 | -13.8518 | -13.9 | 836 | 34.8333
| 837 | -13.8518 | 428.5432 | -13.8852 | -13.9 | 837 | 34.875
| 838 | -13.8852 | 427.9973 | -13.9184 | -13.9 | 838 | 34.9167
| 839 | -13.9184 | 427.452 | -13.9516 | -14 | 839 | 34.9583
| 840 | -13.9516 | 426.9075 | -13.9848 | -14 | 840 | 35
| 841 | -13.9848 | 426.3636 | -14.018 | -14 | 841 | 35.0417
| 842 | -14.018 | 425.8205 | -14.0511 | -14.1 | 842 | 35.0833
| 843 | -14.0511 | 425.278 | -14.0841 | -14.1 | 843 | 35.125
| 844 | -14.0841 | 424.7362 | -14.1171 | -14.1 | 844 | 35.1667
| 845 | -14.1171 | 424.1952 | -14.1501 | -14.2 | 845 | 35.2083
| 846 | -14.1501 | 423.6548 | -14.183 | -14.2 | 846 | 35.25
| 847 | -14.183 | 423.1151 | -14.2159 | -14.2 | 847 | 35.2917
| 848 | -14.2159 | 422.576 | -14.2488 | -14.2 | 848 | 35.3333
| 849 | -14.2488 | 422.0377 | -14.2816 | -14.3 | 849 | 35.375
| 850 | -14.2816 | 421.5001 | -14.3144 | -14.3 | 850 | 35.4167
| 851 | -14.3144 | 420.9631 | -14.3471 | -14.3 | 851 | 35.4583
| 852 | -14.3471 | 420.4268 | -14.3798 | -14.4 | 852 | 35.5
| 853 | -14.3798 | 419.8912 | -14.4124 | -14.4 | 853 | 35.5417
| 854 | -14.4124 | 419.3563 | -14.445 | -14.4 | 854 | 35.5833
| 855 | -14.445 | 418.8221 | -14.4775 | -14.5 | 855 | 35.625
| 856 | -14.4775 | 418.2886 | -14.5101 | -14.5 | 856 | 35.6667
| 857 | -14.5101 | 417.7557 | -14.5425 | -14.5 | 857 | 35.7083
| 858 | -14.5425 | 417.2235 | -14.575 | -14.6 | 858 | 35.75
| 859 | -14.575 | 416.692 | -14.6074 | -14.6 | 859 | 35.7917
| 860 | -14.6074 | 416.1611 | -14.6397 | -14.6 | 860 | 35.8333
| 861 | -14.6397 | 415.631 | -14.672 | -14.7 | 861 | 35.875
| 862 | -14.672 | 415.1015 | -14.7043 | -14.7 | 862 | 35.9167
| 863 | -14.7043 | 414.5727 | -14.7365 | -14.7 | 863 | 35.9583
| 864 | -14.7365 | 414.0446 | -14.7687 | -14.8 | 864 | 36
| 865 | -14.7687 | 413.5171 | -14.8008 | -14.8 | 865 | 36.0417
| 866 | -14.8008 | 412.9903 | -14.8329 | -14.8 | 866 | 36.0833
| 867 | -14.8329 | 412.4642 | -14.865 | -14.9 | 867 | 36.125
| 868 | -14.865 | 411.9387 | -14.897 | -14.9 | 868 | 36.1667
| 869 | -14.897 | 411.414 | -14.929 | -14.9 | 869 | 36.2083
| 870 | -14.929 | 410.8899 | -14.9609 | -15 | 870 | 36.25
| 871 | -14.9609 | 410.3664 | -14.9928 | -15 | 871 | 36.2917
| 872 | -14.9928 | 409.8436 | -15.0247 | -15 | 872 | 36.3333
| 873 | -15.0247 | 409.3215 | -15.0565 | -15.1 | 873 | 36.375
| 874 | -15.0565 | 408.8001 | -15.0883 | -15.1 | 874 | 36.4167
| 875 | -15.0883 | 408.2793 | -15.12 | -15.1 | 875 | 36.4583
| 876 | -15.12 | 407.7592 | -15.1517 | -15.2 | 876 | 36.5
| 877 | -15.1517 | 407.2397 | -15.1834 | -15.2 | 877 | 36.5417
| 878 | -15.1834 | 406.7209 | -15.215 | -15.2 | 878 | 36.5833
| 879 | -15.215 | 406.2028 | -15.2465 | -15.2 | 879 | 36.625
| 880 | -15.2465 | 405.6853 | -15.2781 | -15.3 | 880 | 36.6667
| 881 | -15.2781 | 405.1685 | -15.3096 | -15.3 | 881 | 36.7083
| 882 | -15.3096 | 404.6524 | -15.341 | -15.3 | 882 | 36.75
| 883 | -15.341 | 404.1369 | -15.3724 | -15.4 | 883 | 36.7917
| 884 | -15.3724 | 403.622 | -15.4038 | -15.4 | 884 | 36.8333
| 885 | -15.4038 | 403.1079 | -15.4352 | -15.4 | 885 | 36.875
| 886 | -15.4352 | 402.5943 | -15.4664 | -15.5 | 886 | 36.9167
| 887 | -15.4664 | 402.0814 | -15.4977 | -15.5 | 887 | 36.9583
| 888 | -15.4977 | 401.5692 | -15.5289 | -15.5 | 888 | 37
| 889 | -15.5289 | 401.0577 | -15.5601 | -15.6 | 889 | 37.0417
| 890 | -15.5601 | 400.5467 | -15.5912 | -15.6 | 890 | 37.0833
| 891 | -15.5912 | 400.0365 | -15.6223 | -15.6 | 891 | 37.125
| 892 | -15.6223 | 399.5269 | -15.6534 | -15.7 | 892 | 37.1667
| 893 | -15.6534 | 399.0179 | -15.6844 | -15.7 | 893 | 37.2083
| 894 | -15.6844 | 398.5096 | -15.7154 | -15.7 | 894 | 37.25
| 895 | -15.7154 | 398.0019 | -15.7463 | -15.7 | 895 | 37.2917
| 896 | -15.7463 | 397.4949 | -15.7772 | -15.8 | 896 | 37.3333
| 897 | -15.7772 | 396.9885 | -15.8081 | -15.8 | 897 | 37.375
| 898 | -15.8081 | 396.4828 | -15.8389 | -15.8 | 898 | 37.4167
| 899 | -15.8389 | 395.9777 | -15.8697 | -15.9 | 899 | 37.4583
| 900 | -15.8697 | 395.4732 | -15.9004 | -15.9 | 900 | 37.5
| 901 | -15.9004 | 394.9694 | -15.9311 | -15.9 | 901 | 37.5417
| 902 | -15.9311 | 394.4663 | -15.9618 | -16 | 902 | 37.5833
| 903 | -15.9618 | 393.9637 | -15.9924 | -16 | 903 | 37.625
| 904 | -15.9924 | 393.4619 | -16.023 | -16 | 904 | 37.6667
| 905 | -16.023 | 392.9606 | -16.0535 | -16.1 | 905 | 37.7083
| 906 | -16.0535 | 392.46 | -16.084 | -16.1 | 906 | 37.75
| 907 | -16.084 | 391.9601 | -16.1145 | -16.1 | 907 | 37.7917
| 908 | -16.1145 | 391.4607 | -16.1449 | -16.1 | 908 | 37.8333
| 909 | -16.1449 | 390.962 | -16.1753 | -16.2 | 909 | 37.875
| 910 | -16.1753 | 390.464 | -16.2057 | -16.2 | 910 | 37.9167
| 911 | -16.2057 | 389.9666 | -16.236 | -16.2 | 911 | 37.9583
| 912 | -16.236 | 389.4698 | -16.2662 | -16.3 | 912 | 38
| 913 | -16.2662 | 388.9736 | -16.2965 | -16.3 | 913 | 38.0417
| 914 | -16.2965 | 388.4781 | -16.3267 | -16.3 | 914 | 38.0833
| 915 | -16.3267 | 387.9832 | -16.3568 | -16.4 | 915 | 38.125
| 916 | -16.3568 | 387.4889 | -16.3869 | -16.4 | 916 | 38.1667
| 917 | -16.3869 | 386.9953 | -16.417 | -16.4 | 917 | 38.2083
| 918 | -16.417 | 386.5023 | -16.4471 | -16.4 | 918 | 38.25
| 919 | -16.4471 | 386.0099 | -16.4771 | -16.5 | 919 | 38.2917
| 920 | -16.4771 | 385.5182 | -16.507 | -16.5 | 920 | 38.3333
| 921 | -16.507 | 385.0271 | -16.537 | -16.5 | 921 | 38.375
| 922 | -16.537 | 384.5366 | -16.5669 | -16.6 | 922 | 38.4167
| 923 | -16.5669 | 384.0467 | -16.5967 | -16.6 | 923 | 38.4583
| 924 | -16.5967 | 383.5574 | -16.6265 | -16.6 | 924 | 38.5
| 925 | -16.6265 | 383.0688 | -16.6563 | -16.7 | 925 | 38.5417
| 926 | -16.6563 | 382.5808 | -16.686 | -16.7 | 926 | 38.5833
| 927 | -16.686 | 382.0934 | -16.7157 | -16.7 | 927 | 38.625
| 928 | -16.7157 | 381.6067 | -16.7454 | -16.7 | 928 | 38.6667
| 929 | -16.7454 | 381.1205 | -16.775 | -16.8 | 929 | 38.7083
| 930 | -16.775 | 380.635 | -16.8046 | -16.8 | 930 | 38.75
| 931 | -16.8046 | 380.1501 | -16.8342 | -16.8 | 931 | 38.7917
| 932 | -16.8342 | 379.6658 | -16.8637 | -16.9 | 932 | 38.8333
| 933 | -16.8637 | 379.1822 | -16.8931 | -16.9 | 933 | 38.875
| 934 | -16.8931 | 378.6991 | -16.9226 | -16.9 | 934 | 38.9167
| 935 | -16.9226 | 378.2167 | -16.952 | -17 | 935 | 38.9583
| 936 | -16.952 | 377.7349 | -16.9813 | -17 | 936 | 39
| 937 | -16.9813 | 377.2537 | -17.0107 | -17 | 937 | 39.0417
| 938 | -17.0107 | 376.7731 | -17.04 | -17 | 938 | 39.0833
| 939 | -17.04 | 376.2931 | -17.0692 | -17.1 | 939 | 39.125
| 940 | -17.0692 | 375.8137 | -17.0984 | -17.1 | 940 | 39.1667
| 941 | -17.0984 | 375.335 | -17.1276 | -17.1 | 941 | 39.2083
| 942 | -17.1276 | 374.8568 | -17.1567 | -17.2 | 942 | 39.25
| 943 | -17.1567 | 374.3793 | -17.1858 | -17.2 | 943 | 39.2917
| 944 | -17.1858 | 373.9024 | -17.2149 | -17.2 | 944 | 39.3333
| 945 | -17.2149 | 373.426 | -17.2439 | -17.2 | 945 | 39.375
| 946 | -17.2439 | 372.9503 | -17.2729 | -17.3 | 946 | 39.4167
| 947 | -17.2729 | 372.4752 | -17.3019 | -17.3 | 947 | 39.4583
| 948 | -17.3019 | 372.0007 | -17.3308 | -17.3 | 948 | 39.5
| 949 | -17.3308 | 371.5268 | -17.3597 | -17.4 | 949 | 39.5417
| 950 | -17.3597 | 371.0535 | -17.3885 | -17.4 | 950 | 39.5833
| 951 | -17.3885 | 370.5808 | -17.4173 | -17.4 | 951 | 39.625
| 952 | -17.4173 | 370.1087 | -17.4461 | -17.4 | 952 | 39.6667
| 953 | -17.4461 | 369.6372 | -17.4748 | -17.5 | 953 | 39.7083
| 954 | -17.4748 | 369.1663 | -17.5035 | -17.5 | 954 | 39.75
| 955 | -17.5035 | 368.696 | -17.5322 | -17.5 | 955 | 39.7917
| 956 | -17.5322 | 368.2264 | -17.5608 | -17.6 | 956 | 39.8333
| 957 | -17.5608 | 367.7573 | -17.5894 | -17.6 | 957 | 39.875
| 958 | -17.5894 | 367.2888 | -17.6179 | -17.6 | 958 | 39.9167
| 959 | -17.6179 | 366.8209 | -17.6464 | -17.6 | 959 | 39.9583
| 960 | -17.6464 | 366.3536 | -17.6749 | -17.7 | 960 | 40
| 961 | -17.6749 | 365.8869 | -17.7033 | -17.7 | 961 | 40.0417
| 962 | -17.7033 | 365.4207 | -17.7318 | -17.7 | 962 | 40.0833
| 963 | -17.7318 | 364.9552 | -17.7601 | -17.8 | 963 | 40.125
| 964 | -17.7601 | 364.4903 | -17.7885 | -17.8 | 964 | 40.1667
| 965 | -17.7885 | 364.026 | -17.8167 | -17.8 | 965 | 40.2083
| 966 | -17.8167 | 363.5622 | -17.845 | -17.8 | 966 | 40.25
| 967 | -17.845 | 363.0991 | -17.8732 | -17.9 | 967 | 40.2917
| 968 | -17.8732 | 362.6365 | -17.9014 | -17.9 | 968 | 40.3333
| 969 | -17.9014 | 362.1745 | -17.9296 | -17.9 | 969 | 40.375
| 970 | -17.9296 | 361.7132 | -17.9577 | -18 | 970 | 40.4167
| 971 | -17.9577 | 361.2524 | -17.9858 | -18 | 971 | 40.4583
| 972 | -17.9858 | 360.7922 | -18.0138 | -18 | 972 | 40.5
| 973 | -18.0138 | 360.3325 | -18.0418 | -18 | 973 | 40.5417
| 974 | -18.0418 | 359.8735 | -18.0698 | -18.1 | 974 | 40.5833
| 975 | -18.0698 | 359.415 | -18.0977 | -18.1 | 975 | 40.625
| 976 | -18.0977 | 358.9572 | -18.1256 | -18.1 | 976 | 40.6667
| 977 | -18.1256 | 358.4999 | -18.1535 | -18.2 | 977 | 40.7083
| 978 | -18.1535 | 358.0432 | -18.1813 | -18.2 | 978 | 40.75
| 979 | -18.1813 | 357.5871 | -18.2091 | -18.2 | 979 | 40.7917
| 980 | -18.2091 | 357.1315 | -18.2369 | -18.2 | 980 | 40.8333
| 981 | -18.2369 | 356.6766 | -18.2646 | -18.3 | 981 | 40.875
| 982 | -18.2646 | 356.2222 | -18.2923 | -18.3 | 982 | 40.9167
| 983 | -18.2923 | 355.7684 | -18.32 | -18.3 | 983 | 40.9583
| 984 | -18.32 | 355.3152 | -18.3476 | -18.3 | 984 | 41
| 985 | -18.3476 | 354.8625 | -18.3752 | -18.4 | 985 | 41.0417
| 986 | -18.3752 | 354.4105 | -18.4027 | -18.4 | 986 | 41.0833
| 987 | -18.4027 | 353.959 | -18.4302 | -18.4 | 987 | 41.125
| 988 | -18.4302 | 353.508 | -18.4577 | -18.5 | 988 | 41.1667
| 989 | -18.4577 | 353.0577 | -18.4851 | -18.5 | 989 | 41.2083
| 990 | -18.4851 | 352.6079 | -18.5125 | -18.5 | 990 | 41.25
| 991 | -18.5125 | 352.1587 | -18.5399 | -18.5 | 991 | 41.2917
| 992 | -18.5399 | 351.7101 | -18.5673 | -18.6 | 992 | 41.3333
| 993 | -18.5673 | 351.2621 | -18.5946 | -18.6 | 993 | 41.375
| 994 | -18.5946 | 350.8146 | -18.6218 | -18.6 | 994 | 41.4167
| 995 | -18.6218 | 350.3677 | -18.6491 | -18.6 | 995 | 41.4583
| 996 | -18.6491 | 349.9213 | -18.6763 | -18.7 | 996 | 41.5
| 997 | -18.6763 | 349.4756 | -18.7034 | -18.7 | 997 | 41.5417
| 998 | -18.7034 | 349.0304 | -18.7306 | -18.7 | 998 | 41.5833
| 999 | -18.7306 | 348.5857 | -18.7577 | -18.8 | 999 | 41.625
| 1000 | -18.7577 | 348.1416 | -18.7847 | -18.8 | 1000 | 41.6667
| 1001 | -18.7847 | 347.6981 | -18.8117 | -18.8 | 1001 | 41.7083
| 1002 | -18.8117 | 347.2552 | -18.8387 | -18.8 | 1002 | 41.75
| 1003 | -18.8387 | 346.8128 | -18.8657 | -18.9 | 1003 | 41.7917
| 1004 | -18.8657 | 346.371 | -18.8926 | -18.9 | 1004 | 41.8333
| 1005 | -18.8926 | 345.9298 | -18.9195 | -18.9 | 1005 | 41.875
| 1006 | -18.9195 | 345.4891 | -18.9464 | -18.9 | 1006 | 41.9167
| 1007 | -18.9464 | 345.0489 | -18.9732 | -19 | 1007 | 41.9583
| 1008 | -18.9732 | 344.6094 | -19 | -19 | 1008 | 42
| 1009 | -19 | 344.1704 | -19.0267 | -19 | 1009 | 42.0417
| 1010 | -19.0267 | 343.7319 | -19.0534 | -19.1 | 1010 | 42.0833
| 1011 | -19.0534 | 343.294 | -19.0801 | -19.1 | 1011 | 42.125
| 1012 | -19.0801 | 342.8567 | -19.1068 | -19.1 | 1012 | 42.1667
| 1013 | -19.1068 | 342.4199 | -19.1334 | -19.1 | 1013 | 42.2083
| 1014 | -19.1334 | 341.9837 | -19.16 | -19.2 | 1014 | 42.25
| 1015 | -19.16 | 341.548 | -19.1865 | -19.2 | 1015 | 42.2917
| 1016 | -19.1865 | 341.1129 | -19.213 | -19.2 | 1016 | 42.3333
| 1017 | -19.213 | 340.6784 | -19.2395 | -19.2 | 1017 | 42.375
| 1018 | -19.2395 | 340.2444 | -19.266 | -19.3 | 1018 | 42.4167
| 1019 | -19.266 | 339.8109 | -19.2924 | -19.3 | 1019 | 42.4583
| 1020 | -19.2924 | 339.378 | -19.3188 | -19.3 | 1020 | 42.5
| 1021 | -19.3188 | 338.9457 | -19.3451 | -19.3 | 1021 | 42.5417
| 1022 | -19.3451 | 338.5139 | -19.3714 | -19.4 | 1022 | 42.5833
| 1023 | -19.3714 | 338.0827 | -19.3977 | -19.4 | 1023 | 42.625
| 1024 | -19.3977 | 337.652 | -19.4239 | -19.4 | 1024 | 42.6667
| 1025 | -19.4239 | 337.2218 | -19.4502 | -19.5 | 1025 | 42.7083
| 1026 | -19.4502 | 336.7922 | -19.4763 | -19.5 | 1026 | 42.75
| 1027 | -19.4763 | 336.3632 | -19.5025 | -19.5 | 1027 | 42.7917
| 1028 | -19.5025 | 335.9347 | -19.5286 | -19.5 | 1028 | 42.8333
| 1029 | -19.5286 | 335.5067 | -19.5547 | -19.6 | 1029 | 42.875
| 1030 | -19.5547 | 335.0793 | -19.5807 | -19.6 | 1030 | 42.9167
| 1031 | -19.5807 | 334.6525 | -19.6067 | -19.6 | 1031 | 42.9583
| 1032 | -19.6067 | 334.2261 | -19.6327 | -19.6 | 1032 | 43
| 1033 | -19.6327 | 333.8004 | -19.6587 | -19.7 | 1033 | 43.0417
| 1034 | -19.6587 | 333.3751 | -19.6846 | -19.7 | 1034 | 43.0833
| 1035 | -19.6846 | 332.9504 | -19.7104 | -19.7 | 1035 | 43.125
| 1036 | -19.7104 | 332.5263 | -19.7363 | -19.7 | 1036 | 43.1667
| 1037 | -19.7363 | 332.1027 | -19.7621 | -19.8 | 1037 | 43.2083
| 1038 | -19.7621 | 331.6796 | -19.7879 | -19.8 | 1038 | 43.25
| 1039 | -19.7879 | 331.2571 | -19.8136 | -19.8 | 1039 | 43.2917
| 1040 | -19.8136 | 330.8351 | -19.8394 | -19.8 | 1040 | 43.3333
| 1041 | -19.8394 | 330.4136 | -19.865 | -19.9 | 1041 | 43.375
| 1042 | -19.865 | 329.9927 | -19.8907 | -19.9 | 1042 | 43.4167
| 1043 | -19.8907 | 329.5723 | -19.9163 | -19.9 | 1043 | 43.4583
| 1044 | -19.9163 | 329.1524 | -19.9419 | -19.9 | 1044 | 43.5
| 1045 | -19.9419 | 328.7331 | -19.9674 | -20 | 1045 | 43.5417
| 1046 | -19.9674 | 328.3143 | -19.993 | -20 | 1046 | 43.5833
| 1047 | -19.993 | 327.8961 | -20.0185 | -20 | 1047 | 43.625
| 1048 | -20.0185 | 327.4784 | -20.0439 | -20 | 1048 | 43.6667
| 1049 | -20.0439 | 327.0612 | -20.0693 | -20.1 | 1049 | 43.7083
| 1050 | -20.0693 | 326.6445 | -20.0947 | -20.1 | 1050 | 43.75
| 1051 | -20.0947 | 326.2284 | -20.1201 | -20.1 | 1051 | 43.7917
| 1052 | -20.1201 | 325.8128 | -20.1454 | -20.1 | 1052 | 43.8333
| 1053 | -20.1454 | 325.3978 | -20.1707 | -20.2 | 1053 | 43.875
| 1054 | -20.1707 | 324.9832 | -20.196 | -20.2 | 1054 | 43.9167
| 1055 | -20.196 | 324.5692 | -20.2212 | -20.2 | 1055 | 43.9583
| 1056 | -20.2212 | 324.1558 | -20.2464 | -20.2 | 1056 | 44
| 1057 | -20.2464 | 323.7428 | -20.2715 | -20.3 | 1057 | 44.0417
| 1058 | -20.2715 | 323.3304 | -20.2967 | -20.3 | 1058 | 44.0833
| 1059 | -20.2967 | 322.9185 | -20.3218 | -20.3 | 1059 | 44.125
| 1060 | -20.3218 | 322.5071 | -20.3469 | -20.3 | 1060 | 44.1667
| 1061 | -20.3469 | 322.0963 | -20.3719 | -20.4 | 1061 | 44.2083
| 1062 | -20.3719 | 321.6859 | -20.3969 | -20.4 | 1062 | 44.25
| 1063 | -20.3969 | 321.2761 | -20.4219 | -20.4 | 1063 | 44.2917
| 1064 | -20.4219 | 320.8669 | -20.4468 | -20.4 | 1064 | 44.3333
| 1065 | -20.4468 | 320.4581 | -20.4717 | -20.5 | 1065 | 44.375
| 1066 | -20.4717 | 320.0499 | -20.4966 | -20.5 | 1066 | 44.4167
| 1067 | -20.4966 | 319.6421 | -20.5214 | -20.5 | 1067 | 44.4583
| 1068 | -20.5214 | 319.2349 | -20.5463 | -20.5 | 1068 | 44.5
| 1069 | -20.5463 | 318.8283 | -20.571 | -20.6 | 1069 | 44.5417
| 1070 | -20.571 | 318.4221 | -20.5958 | -20.6 | 1070 | 44.5833
| 1071 | -20.5958 | 318.0164 | -20.6205 | -20.6 | 1071 | 44.625
| 1072 | -20.6205 | 317.6113 | -20.6452 | -20.6 | 1072 | 44.6667
| 1073 | -20.6452 | 317.2067 | -20.6699 | -20.7 | 1073 | 44.7083
| 1074 | -20.6699 | 316.8026 | -20.6945 | -20.7 | 1074 | 44.75
| 1075 | -20.6945 | 316.399 | -20.7191 | -20.7 | 1075 | 44.7917
| 1076 | -20.7191 | 315.996 | -20.7436 | -20.7 | 1076 | 44.8333
| 1077 | -20.7436 | 315.5934 | -20.7682 | -20.8 | 1077 | 44.875
| 1078 | -20.7682 | 315.1914 | -20.7927 | -20.8 | 1078 | 44.9167
| 1079 | -20.7927 | 314.7898 | -20.8171 | -20.8 | 1079 | 44.9583
| 1080 | -20.8171 | 314.3888 | -20.8416 | -20.8 | 1080 | 45
| 1081 | -20.8416 | 313.9883 | -20.866 | -20.9 | 1081 | 45.0417
| 1082 | -20.866 | 313.5883 | -20.8904 | -20.9 | 1082 | 45.0833
| 1083 | -20.8904 | 313.1888 | -20.9147 | -20.9 | 1083 | 45.125
| 1084 | -20.9147 | 312.7898 | -20.939 | -20.9 | 1084 | 45.1667
| 1085 | -20.939 | 312.3914 | -20.9633 | -21 | 1085 | 45.2083
| 1086 | -20.9633 | 311.9934 | -20.9875 | -21 | 1086 | 45.25
| 1087 | -20.9875 | 311.5959 | -21.0118 | -21 | 1087 | 45.2917
| 1088 | -21.0118 | 311.199 | -21.036 | -21 | 1088 | 45.3333
| 1089 | -21.036 | 310.8026 | -21.0601 | -21.1 | 1089 | 45.375
| 1090 | -21.0601 | 310.4066 | -21.0842 | -21.1 | 1090 | 45.4167
| 1091 | -21.0842 | 310.0112 | -21.1083 | -21.1 | 1091 | 45.4583
| 1092 | -21.1083 | 309.6163 | -21.1324 | -21.1 | 1092 | 45.5
| 1093 | -21.1324 | 309.2218 | -21.1564 | -21.2 | 1093 | 45.5417
| 1094 | -21.1564 | 308.8279 | -21.1804 | -21.2 | 1094 | 45.5833
| 1095 | -21.1804 | 308.4345 | -21.2044 | -21.2 | 1095 | 45.625
| 1096 | -21.2044 | 308.0416 | -21.2284 | -21.2 | 1096 | 45.6667
| 1097 | -21.2284 | 307.6491 | -21.2523 | -21.3 | 1097 | 45.7083
| 1098 | -21.2523 | 307.2572 | -21.2762 | -21.3 | 1098 | 45.75
| 1099 | -21.2762 | 306.8658 | -21.3 | -21.3 | 1099 | 45.7917
| 1100 | -21.3 | 306.4749 | -21.3238 | -21.3 | 1100 | 45.8333
| 1101 | -21.3238 | 306.0844 | -21.3476 | -21.3 | 1101 | 45.875
| 1102 | -21.3476 | 305.6945 | -21.3714 | -21.4 | 1102 | 45.9167
| 1103 | -21.3714 | 305.3051 | -21.3951 | -21.4 | 1103 | 45.9583
| 1104 | -21.3951 | 304.9161 | -21.4188 | -21.4 | 1104 | 46
| 1105 | -21.4188 | 304.5277 | -21.4425 | -21.4 | 1105 | 46.0417
| 1106 | -21.4425 | 304.1398 | -21.4661 | -21.5 | 1106 | 46.0833
| 1107 | -21.4661 | 303.7523 | -21.4897 | -21.5 | 1107 | 46.125
| 1108 | -21.4897 | 303.3653 | -21.5133 | -21.5 | 1108 | 46.1667
| 1109 | -21.5133 | 302.9789 | -21.5369 | -21.5 | 1109 | 46.2083
| 1110 | -21.5369 | 302.5929 | -21.5604 | -21.6 | 1110 | 46.25
| 1111 | -21.5604 | 302.2074 | -21.5839 | -21.6 | 1111 | 46.2917
| 1112 | -21.5839 | 301.8224 | -21.6073 | -21.6 | 1112 | 46.3333
| 1113 | -21.6073 | 301.4379 | -21.6308 | -21.6 | 1113 | 46.375
| 1114 | -21.6308 | 301.0539 | -21.6542 | -21.7 | 1114 | 46.4167
| 1115 | -21.6542 | 300.6704 | -21.6776 | -21.7 | 1115 | 46.4583
| 1116 | -21.6776 | 300.2874 | -21.7009 | -21.7 | 1116 | 46.5
| 1117 | -21.7009 | 299.9048 | -21.7242 | -21.7 | 1117 | 46.5417
| 1118 | -21.7242 | 299.5228 | -21.7475 | -21.7 | 1118 | 46.5833
| 1119 | -21.7475 | 299.1412 | -21.7707 | -21.8 | 1119 | 46.625
| 1120 | -21.7707 | 298.7601 | -21.794 | -21.8 | 1120 | 46.6667
| 1121 | -21.794 | 298.3795 | -21.8172 | -21.8 | 1121 | 46.7083
| 1122 | -21.8172 | 297.9994 | -21.8403 | -21.8 | 1122 | 46.75
| 1123 | -21.8403 | 297.6198 | -21.8635 | -21.9 | 1123 | 46.7917
| 1124 | -21.8635 | 297.2406 | -21.8866 | -21.9 | 1124 | 46.8333
| 1125 | -21.8866 | 296.862 | -21.9096 | -21.9 | 1125 | 46.875
| 1126 | -21.9096 | 296.4838 | -21.9327 | -21.9 | 1126 | 46.9167
| 1127 | -21.9327 | 296.1061 | -21.9557 | -22 | 1127 | 46.9583
| 1128 | -21.9557 | 295.7289 | -21.9787 | -22 | 1128 | 47
| 1129 | -21.9787 | 295.3521 | -22.0016 | -22 | 1129 | 47.0417
| 1130 | -22.0016 | 294.9759 | -22.0246 | -22 | 1130 | 47.0833
| 1131 | -22.0246 | 294.6001 | -22.0475 | -22 | 1131 | 47.125
| 1132 | -22.0475 | 294.2248 | -22.0703 | -22.1 | 1132 | 47.1667
| 1133 | -22.0703 | 293.85 | -22.0932 | -22.1 | 1133 | 47.2083
| 1134 | -22.0932 | 293.4757 | -22.116 | -22.1 | 1134 | 47.25
| 1135 | -22.116 | 293.1018 | -22.1388 | -22.1 | 1135 | 47.2917
| 1136 | -22.1388 | 292.7284 | -22.1615 | -22.2 | 1136 | 47.3333
| 1137 | -22.1615 | 292.3555 | -22.1843 | -22.2 | 1137 | 47.375
| 1138 | -22.1843 | 291.983 | -22.2069 | -22.2 | 1138 | 47.4167
| 1139 | -22.2069 | 291.6111 | -22.2296 | -22.2 | 1139 | 47.4583
| 1140 | -22.2296 | 291.2396 | -22.2523 | -22.3 | 1140 | 47.5
| 1141 | -22.2523 | 290.8686 | -22.2749 | -22.3 | 1141 | 47.5417
| 1142 | -22.2749 | 290.498 | -22.2974 | -22.3 | 1142 | 47.5833
| 1143 | -22.2974 | 290.128 | -22.32 | -22.3 | 1143 | 47.625
| 1144 | -22.32 | 289.7584 | -22.3425 | -22.3 | 1144 | 47.6667
| 1145 | -22.3425 | 289.3892 | -22.365 | -22.4 | 1145 | 47.7083
| 1146 | -22.365 | 289.0206 | -22.3875 | -22.4 | 1146 | 47.75
| 1147 | -22.3875 | 288.6524 | -22.4099 | -22.4 | 1147 | 47.7917
| 1148 | -22.4099 | 288.2847 | -22.4323 | -22.4 | 1148 | 47.8333
| 1149 | -22.4323 | 287.9174 | -22.4547 | -22.5 | 1149 | 47.875
| 1150 | -22.4547 | 287.5506 | -22.4771 | -22.5 | 1150 | 47.9167
| 1151 | -22.4771 | 287.1843 | -22.4994 | -22.5 | 1151 | 47.9583
| 1152 | -22.4994 | 286.8184 | -22.5217 | -22.5 | 1152 | 48
| 1153 | -22.5217 | 286.4531 | -22.5439 | -22.5 | 1153 | 48.0417
| 1154 | -22.5439 | 286.0881 | -22.5662 | -22.6 | 1154 | 48.0833
| 1155 | -22.5662 | 285.7237 | -22.5884 | -22.6 | 1155 | 48.125
| 1156 | -22.5884 | 285.3597 | -22.6106 | -22.6 | 1156 | 48.1667
| 1157 | -22.6106 | 284.9962 | -22.6327 | -22.6 | 1157 | 48.2083
| 1158 | -22.6327 | 284.6331 | -22.6548 | -22.7 | 1158 | 48.25
| 1159 | -22.6548 | 284.2705 | -22.6769 | -22.7 | 1159 | 48.2917
| 1160 | -22.6769 | 283.9084 | -22.699 | -22.7 | 1160 | 48.3333
| 1161 | -22.699 | 283.5467 | -22.721 | -22.7 | 1161 | 48.375
| 1162 | -22.721 | 283.1855 | -22.7431 | -22.7 | 1162 | 48.4167
| 1163 | -22.7431 | 282.8247 | -22.765 | -22.8 | 1163 | 48.4583
| 1164 | -22.765 | 282.4644 | -22.787 | -22.8 | 1164 | 48.5
| 1165 | -22.787 | 282.1046 | -22.8089 | -22.8 | 1165 | 48.5417
| 1166 | -22.8089 | 281.7452 | -22.8308 | -22.8 | 1166 | 48.5833
| 1167 | -22.8308 | 281.3863 | -22.8527 | -22.9 | 1167 | 48.625
| 1168 | -22.8527 | 281.0278 | -22.8745 | -22.9 | 1168 | 48.6667
| 1169 | -22.8745 | 280.6698 | -22.8964 | -22.9 | 1169 | 48.7083
| 1170 | -22.8964 | 280.3122 | -22.9181 | -22.9 | 1170 | 48.75
| 1171 | -22.9181 | 279.9552 | -22.9399 | -22.9 | 1171 | 48.7917
| 1172 | -22.9399 | 279.5985 | -22.9616 | -23 | 1172 | 48.8333
| 1173 | -22.9616 | 279.2423 | -22.9833 | -23 | 1173 | 48.875
| 1174 | -22.9833 | 278.8866 | -23.005 | -23 | 1174 | 48.9167
| 1175 | -23.005 | 278.5313 | -23.0267 | -23 | 1175 | 48.9583
| 1176 | -23.0267 | 278.1765 | -23.0483 | -23 | 1176 | 49
| 1177 | -23.0483 | 277.8221 | -23.0699 | -23.1 | 1177 | 49.0417
| 1178 | -23.0699 | 277.4682 | -23.0915 | -23.1 | 1178 | 49.0833
| 1179 | -23.0915 | 277.1147 | -23.113 | -23.1 | 1179 | 49.125
| 1180 | -23.113 | 276.7617 | -23.1345 | -23.1 | 1180 | 49.1667
| 1181 | -23.1345 | 276.4091 | -23.156 | -23.2 | 1181 | 49.2083
| 1182 | -23.156 | 276.057 | -23.1775 | -23.2 | 1182 | 49.25
| 1183 | -23.1775 | 275.7053 | -23.1989 | -23.2 | 1183 | 49.2917
| 1184 | -23.1989 | 275.3541 | -23.2203 | -23.2 | 1184 | 49.3333
| 1185 | -23.2203 | 275.0033 | -23.2417 | -23.2 | 1185 | 49.375
| 1186 | -23.2417 | 274.653 | -23.263 | -23.3 | 1186 | 49.4167
| 1187 | -23.263 | 274.3031 | -23.2843 | -23.3 | 1187 | 49.4583
| 1188 | -23.2843 | 273.9536 | -23.3056 | -23.3 | 1188 | 49.5
| 1189 | -23.3056 | 273.6046 | -23.3269 | -23.3 | 1189 | 49.5417
| 1190 | -23.3269 | 273.2561 | -23.3481 | -23.3 | 1190 | 49.5833
| 1191 | -23.3481 | 272.908 | -23.3694 | -23.4 | 1191 | 49.625
| 1192 | -23.3694 | 272.5603 | -23.3905 | -23.4 | 1192 | 49.6667
| 1193 | -23.3905 | 272.2131 | -23.4117 | -23.4 | 1193 | 49.7083
| 1194 | -23.4117 | 271.8663 | -23.4328 | -23.4 | 1194 | 49.75
| 1195 | -23.4328 | 271.52 | -23.4539 | -23.5 | 1195 | 49.7917
| 1196 | -23.4539 | 271.1741 | -23.475 | -23.5 | 1196 | 49.8333
| 1197 | -23.475 | 270.8286 | -23.4961 | -23.5 | 1197 | 49.875
| 1198 | -23.4961 | 270.4836 | -23.5171 | -23.5 | 1198 | 49.9167
| 1199 | -23.5171 | 270.139 | -23.5381 | -23.5 | 1199 | 49.9583
| 1200 | -23.5381 | 269.7949 | -23.5591 | -23.6 | 1200 | 50
| 1201 | -23.5591 | 269.4512 | -23.58 | -23.6 | 1201 | 50.0417
| 1202 | -23.58 | 269.1079 | -23.6009 | -23.6 | 1202 | 50.0833
| 1203 | -23.6009 | 268.7651 | -23.6218 | -23.6 | 1203 | 50.125
| 1204 | -23.6218 | 268.4227 | -23.6427 | -23.6 | 1204 | 50.1667
| 1205 | -23.6427 | 268.0808 | -23.6635 | -23.7 | 1205 | 50.2083
| 1206 | -23.6635 | 267.7393 | -23.6843 | -23.7 | 1206 | 50.25
| 1207 | -23.6843 | 267.3982 | -23.7051 | -23.7 | 1207 | 50.2917
| 1208 | -23.7051 | 267.0575 | -23.7259 | -23.7 | 1208 | 50.3333
| 1209 | -23.7259 | 266.7173 | -23.7466 | -23.7 | 1209 | 50.375
| 1210 | -23.7466 | 266.3776 | -23.7673 | -23.8 | 1210 | 50.4167
| 1211 | -23.7673 | 266.0382 | -23.788 | -23.8 | 1211 | 50.4583
| 1212 | -23.788 | 265.6993 | -23.8086 | -23.8 | 1212 | 50.5
| 1213 | -23.8086 | 265.3608 | -23.8293 | -23.8 | 1213 | 50.5417
| 1214 | -23.8293 | 265.0228 | -23.8499 | -23.8 | 1214 | 50.5833
| 1215 | -23.8499 | 264.6851 | -23.8704 | -23.9 | 1215 | 50.625
| 1216 | -23.8704 | 264.348 | -23.891 | -23.9 | 1216 | 50.6667
| 1217 | -23.891 | 264.0112 | -23.9115 | -23.9 | 1217 | 50.7083
| 1218 | -23.9115 | 263.6749 | -23.932 | -23.9 | 1218 | 50.75
| 1219 | -23.932 | 263.339 | -23.9525 | -24 | 1219 | 50.7917
| 1220 | -23.9525 | 263.0035 | -23.9729 | -24 | 1220 | 50.8333
| 1221 | -23.9729 | 262.6684 | -23.9933 | -24 | 1221 | 50.875
| 1222 | -23.9933 | 262.3338 | -24.0137 | -24 | 1222 | 50.9167
| 1223 | -24.0137 | 261.9996 | -24.0341 | -24 | 1223 | 50.9583
| 1224 | -24.0341 | 261.6659 | -24.0544 | -24.1 | 1224 | 51
| 1225 | -24.0544 | 261.3325 | -24.0747 | -24.1 | 1225 | 51.0417
| 1226 | -24.0747 | 260.9996 | -24.095 | -24.1 | 1226 | 51.0833
| 1227 | -24.095 | 260.6671 | -24.1153 | -24.1 | 1227 | 51.125
| 1228 | -24.1153 | 260.335 | -24.1355 | -24.1 | 1228 | 51.1667
| 1229 | -24.1355 | 260.0034 | -24.1557 | -24.2 | 1229 | 51.2083
| 1230 | -24.1557 | 259.6722 | -24.1759 | -24.2 | 1230 | 51.25
| 1231 | -24.1759 | 259.3414 | -24.1961 | -24.2 | 1231 | 51.2917
| 1232 | -24.1961 | 259.011 | -24.2162 | -24.2 | 1232 | 51.3333
| 1233 | -24.2162 | 258.681 | -24.2363 | -24.2 | 1233 | 51.375
| 1234 | -24.2363 | 258.3515 | -24.2564 | -24.3 | 1234 | 51.4167
| 1235 | -24.2564 | 258.0224 | -24.2765 | -24.3 | 1235 | 51.4583
| 1236 | -24.2765 | 257.6937 | -24.2965 | -24.3 | 1236 | 51.5
| 1237 | -24.2965 | 257.3654 | -24.3165 | -24.3 | 1237 | 51.5417
| 1238 | -24.3165 | 257.0375 | -24.3365 | -24.3 | 1238 | 51.5833
| 1239 | -24.3365 | 256.7101 | -24.3564 | -24.4 | 1239 | 51.625
| 1240 | -24.3564 | 256.383 | -24.3764 | -24.4 | 1240 | 51.6667
| 1241 | -24.3764 | 256.0564 | -24.3963 | -24.4 | 1241 | 51.7083
| 1242 | -24.3963 | 255.7302 | -24.4161 | -24.4 | 1242 | 51.75
| 1243 | -24.4161 | 255.4045 | -24.436 | -24.4 | 1243 | 51.7917
| 1244 | -24.436 | 255.0791 | -24.4558 | -24.5 | 1244 | 51.8333
| 1245 | -24.4558 | 254.7541 | -24.4756 | -24.5 | 1245 | 51.875
| 1246 | -24.4756 | 254.4296 | -24.4954 | -24.5 | 1246 | 51.9167
| 1247 | -24.4954 | 254.1055 | -24.5152 | -24.5 | 1247 | 51.9583
| 1248 | -24.5152 | 253.7818 | -24.5349 | -24.5 | 1248 | 52
| 1249 | -24.5349 | 253.4585 | -24.5546 | -24.6 | 1249 | 52.0417
| 1250 | -24.5546 | 253.1356 | -24.5743 | -24.6 | 1250 | 52.0833
| 1251 | -24.5743 | 252.8131 | -24.5939 | -24.6 | 1251 | 52.125
| 1252 | -24.5939 | 252.491 | -24.6135 | -24.6 | 1252 | 52.1667
| 1253 | -24.6135 | 252.1694 | -24.6331 | -24.6 | 1253 | 52.2083
| 1254 | -24.6331 | 251.8481 | -24.6527 | -24.7 | 1254 | 52.25
| 1255 | -24.6527 | 251.5273 | -24.6723 | -24.7 | 1255 | 52.2917
| 1256 | -24.6723 | 251.2069 | -24.6918 | -24.7 | 1256 | 52.3333
| 1257 | -24.6918 | 250.8869 | -24.7113 | -24.7 | 1257 | 52.375
| 1258 | -24.7113 | 250.5672 | -24.7308 | -24.7 | 1258 | 52.4167
| 1259 | -24.7308 | 250.248 | -24.7502 | -24.8 | 1259 | 52.4583
| 1260 | -24.7502 | 249.9292 | -24.7696 | -24.8 | 1260 | 52.5
| 1261 | -24.7696 | 249.6109 | -24.7891 | -24.8 | 1261 | 52.5417
| 1262 | -24.7891 | 249.2929 | -24.8084 | -24.8 | 1262 | 52.5833
| 1263 | -24.8084 | 248.9753 | -24.8278 | -24.8 | 1263 | 52.625
| 1264 | -24.8278 | 248.6581 | -24.8471 | -24.8 | 1264 | 52.6667
| 1265 | -24.8471 | 248.3413 | -24.8664 | -24.9 | 1265 | 52.7083
| 1266 | -24.8664 | 248.025 | -24.8857 | -24.9 | 1266 | 52.75
| 1267 | -24.8857 | 247.709 | -24.9049 | -24.9 | 1267 | 52.7917
| 1268 | -24.9049 | 247.3934 | -24.9242 | -24.9 | 1268 | 52.8333
| 1269 | -24.9242 | 247.0783 | -24.9434 | -24.9 | 1269 | 52.875
| 1270 | -24.9434 | 246.7635 | -24.9626 | -25 | 1270 | 52.9167
| 1271 | -24.9626 | 246.4492 | -24.9817 | -25 | 1271 | 52.9583
| 1272 | -24.9817 | 246.1352 | -25.0009 | -25 | 1272 | 53
| 1273 | -25.0009 | 245.8216 | -25.02 | -25 | 1273 | 53.0417
| 1274 | -25.02 | 245.5085 | -25.039 | -25 | 1274 | 53.0833
| 1275 | -25.039 | 245.1957 | -25.0581 | -25.1 | 1275 | 53.125
| 1276 | -25.0581 | 244.8834 | -25.0771 | -25.1 | 1276 | 53.1667
| 1277 | -25.0771 | 244.5714 | -25.0961 | -25.1 | 1277 | 53.2083
| 1278 | -25.0961 | 244.2598 | -25.1151 | -25.1 | 1278 | 53.25
| 1279 | -25.1151 | 243.9487 | -25.1341 | -25.1 | 1279 | 53.2917
| 1280 | -25.1341 | 243.6379 | -25.153 | -25.2 | 1280 | 53.3333
| 1281 | -25.153 | 243.3275 | -25.1719 | -25.2 | 1281 | 53.375
| 1282 | -25.1719 | 243.0175 | -25.1908 | -25.2 | 1282 | 53.4167
| 1283 | -25.1908 | 242.708 | -25.2097 | -25.2 | 1283 | 53.4583
| 1284 | -25.2097 | 242.3988 | -25.2285 | -25.2 | 1284 | 53.5
| 1285 | -25.2285 | 242.09 | -25.2474 | -25.2 | 1285 | 53.5417
| 1286 | -25.2474 | 241.7816 | -25.2662 | -25.3 | 1286 | 53.5833
| 1287 | -25.2662 | 241.4736 | -25.2849 | -25.3 | 1287 | 53.625
| 1288 | -25.2849 | 241.1659 | -25.3037 | -25.3 | 1288 | 53.6667
| 1289 | -25.3037 | 240.8587 | -25.3224 | -25.3 | 1289 | 53.7083
| 1290 | -25.3224 | 240.5519 | -25.3411 | -25.3 | 1290 | 53.75
| 1291 | -25.3411 | 240.2454 | -25.3598 | -25.4 | 1291 | 53.7917
| 1292 | -25.3598 | 239.9394 | -25.3784 | -25.4 | 1292 | 53.8333
| 1293 | -25.3784 | 239.6337 | -25.397 | -25.4 | 1293 | 53.875
| 1294 | -25.397 | 239.3284 | -25.4156 | -25.4 | 1294 | 53.9167
| 1295 | -25.4156 | 239.0235 | -25.4342 | -25.4 | 1295 | 53.9583
| 1296 | -25.4342 | 238.719 | -25.4528 | -25.5 | 1296 | 54
| 1297 | -25.4528 | 238.4149 | -25.4713 | -25.5 | 1297 | 54.0417
| 1298 | -25.4713 | 238.1112 | -25.4898 | -25.5 | 1298 | 54.0833
| 1299 | -25.4898 | 237.8079 | -25.5083 | -25.5 | 1299 | 54.125
| 1300 | -25.5083 | 237.5049 | -25.5268 | -25.5 | 1300 | 54.1667
| 1301 | -25.5268 | 237.2024 | -25.5452 | -25.5 | 1301 | 54.2083
| 1302 | -25.5452 | 236.9002 | -25.5636 | -25.6 | 1302 | 54.25
| 1303 | -25.5636 | 236.5984 | -25.582 | -25.6 | 1303 | 54.2917
| 1304 | -25.582 | 236.297 | -25.6004 | -25.6 | 1304 | 54.3333
| 1305 | -25.6004 | 235.996 | -25.6187 | -25.6 | 1305 | 54.375
| 1306 | -25.6187 | 235.6953 | -25.637 | -25.6 | 1306 | 54.4167
| 1307 | -25.637 | 235.3951 | -25.6553 | -25.7 | 1307 | 54.4583
| 1308 | -25.6553 | 235.0952 | -25.6736 | -25.7 | 1308 | 54.5
| 1309 | -25.6736 | 234.7957 | -25.6919 | -25.7 | 1309 | 54.5417
| 1310 | -25.6919 | 234.4966 | -25.7101 | -25.7 | 1310 | 54.5833
| 1311 | -25.7101 | 234.1979 | -25.7283 | -25.7 | 1311 | 54.625
| 1312 | -25.7283 | 233.8995 | -25.7465 | -25.7 | 1312 | 54.6667
| 1313 | -25.7465 | 233.6015 | -25.7646 | -25.8 | 1313 | 54.7083
| 1314 | -25.7646 | 233.3039 | -25.7828 | -25.8 | 1314 | 54.75
| 1315 | -25.7828 | 233.0067 | -25.8009 | -25.8 | 1315 | 54.7917
| 1316 | -25.8009 | 232.7099 | -25.819 | -25.8 | 1316 | 54.8333
| 1317 | -25.819 | 232.4134 | -25.837 | -25.8 | 1317 | 54.875
| 1318 | -25.837 | 232.1174 | -25.8551 | -25.9 | 1318 | 54.9167
| 1319 | -25.8551 | 231.8217 | -25.8731 | -25.9 | 1319 | 54.9583
| 1320 | -25.8731 | 231.5263 | -25.8911 | -25.9 | 1320 | 55
| 1321 | -25.8911 | 231.2314 | -25.9091 | -25.9 | 1321 | 55.0417
| 1322 | -25.9091 | 230.9368 | -25.927 | -25.9 | 1322 | 55.0833
| 1323 | -25.927 | 230.6426 | -25.9449 | -25.9 | 1323 | 55.125
| 1324 | -25.9449 | 230.3488 | -25.9629 | -26 | 1324 | 55.1667
| 1325 | -25.9629 | 230.0554 | -25.9807 | -26 | 1325 | 55.2083
| 1326 | -25.9807 | 229.7623 | -25.9986 | -26 | 1326 | 55.25
| 1327 | -25.9986 | 229.4696 | -26.0164 | -26 | 1327 | 55.2917
| 1328 | -26.0164 | 229.1773 | -26.0342 | -26 | 1328 | 55.3333
| 1329 | -26.0342 | 228.8853 | -26.052 | -26.1 | 1329 | 55.375
| 1330 | -26.052 | 228.5937 | -26.0698 | -26.1 | 1330 | 55.4167
| 1331 | -26.0698 | 228.3025 | -26.0876 | -26.1 | 1331 | 55.4583
| 1332 | -26.0876 | 228.0117 | -26.1053 | -26.1 | 1332 | 55.5
| 1333 | -26.1053 | 227.7212 | -26.123 | -26.1 | 1333 | 55.5417
| 1334 | -26.123 | 227.4311 | -26.1407 | -26.1 | 1334 | 55.5833
| 1335 | -26.1407 | 227.1414 | -26.1583 | -26.2 | 1335 | 55.625
| 1336 | -26.1583 | 226.852 | -26.1759 | -26.2 | 1336 | 55.6667
| 1337 | -26.1759 | 226.563 | -26.1936 | -26.2 | 1337 | 55.7083
| 1338 | -26.1936 | 226.2744 | -26.2111 | -26.2 | 1338 | 55.75
| 1339 | -26.2111 | 225.9861 | -26.2287 | -26.2 | 1339 | 55.7917
| 1340 | -26.2287 | 225.6982 | -26.2463 | -26.2 | 1340 | 55.8333
| 1341 | -26.2463 | 225.4107 | -26.2638 | -26.3 | 1341 | 55.875
| 1342 | -26.2638 | 225.1236 | -26.2813 | -26.3 | 1342 | 55.9167
| 1343 | -26.2813 | 224.8368 | -26.2987 | -26.3 | 1343 | 55.9583
| 1344 | -26.2987 | 224.5503 | -26.3162 | -26.3 | 1344 | 56
| 1345 | -26.3162 | 224.2643 | -26.3336 | -26.3 | 1345 | 56.0417
| 1346 | -26.3336 | 223.9786 | -26.351 | -26.4 | 1346 | 56.0833
| 1347 | -26.351 | 223.6933 | -26.3684 | -26.4 | 1347 | 56.125
| 1348 | -26.3684 | 223.4083 | -26.3858 | -26.4 | 1348 | 56.1667
| 1349 | -26.3858 | 223.1237 | -26.4031 | -26.4 | 1349 | 56.2083
| 1350 | -26.4031 | 222.8394 | -26.4205 | -26.4 | 1350 | 56.25
| 1351 | -26.4205 | 222.5556 | -26.4378 | -26.4 | 1351 | 56.2917
| 1352 | -26.4378 | 222.272 | -26.455 | -26.5 | 1352 | 56.3333
| 1353 | -26.455 | 221.9889 | -26.4723 | -26.5 | 1353 | 56.375
| 1354 | -26.4723 | 221.7061 | -26.4895 | -26.5 | 1354 | 56.4167
| 1355 | -26.4895 | 221.4237 | -26.5067 | -26.5 | 1355 | 56.4583
| 1356 | -26.5067 | 221.1416 | -26.5239 | -26.5 | 1356 | 56.5
| 1357 | -26.5239 | 220.8599 | -26.5411 | -26.5 | 1357 | 56.5417
| 1358 | -26.5411 | 220.5785 | -26.5582 | -26.6 | 1358 | 56.5833
| 1359 | -26.5582 | 220.2975 | -26.5754 | -26.6 | 1359 | 56.625
| 1360 | -26.5754 | 220.0169 | -26.5925 | -26.6 | 1360 | 56.6667
| 1361 | -26.5925 | 219.7366 | -26.6095 | -26.6 | 1361 | 56.7083
| 1362 | -26.6095 | 219.4566 | -26.6266 | -26.6 | 1362 | 56.75
| 1363 | -26.6266 | 219.1771 | -26.6436 | -26.6 | 1363 | 56.7917
| 1364 | -26.6436 | 218.8979 | -26.6607 | -26.7 | 1364 | 56.8333
| 1365 | -26.6607 | 218.619 | -26.6777 | -26.7 | 1365 | 56.875
| 1366 | -26.6777 | 218.3405 | -26.6946 | -26.7 | 1366 | 56.9167
| 1367 | -26.6946 | 218.0623 | -26.7116 | -26.7 | 1367 | 56.9583
| 1368 | -26.7116 | 217.7846 | -26.7285 | -26.7 | 1368 | 57
| 1369 | -26.7285 | 217.5071 | -26.7454 | -26.7 | 1369 | 57.0417
| 1370 | -26.7454 | 217.23 | -26.7623 | -26.8 | 1370 | 57.0833
| 1371 | -26.7623 | 216.9533 | -26.7792 | -26.8 | 1371 | 57.125
| 1372 | -26.7792 | 216.6769 | -26.796 | -26.8 | 1372 | 57.1667
| 1373 | -26.796 | 216.4009 | -26.8128 | -26.8 | 1373 | 57.2083
| 1374 | -26.8128 | 216.1252 | -26.8296 | -26.8 | 1374 | 57.25
| 1375 | -26.8296 | 215.8499 | -26.8464 | -26.8 | 1375 | 57.2917
| 1376 | -26.8464 | 215.5749 | -26.8632 | -26.9 | 1376 | 57.3333
| 1377 | -26.8632 | 215.3003 | -26.8799 | -26.9 | 1377 | 57.375
| 1378 | -26.8799 | 215.026 | -26.8966 | -26.9 | 1378 | 57.4167
| 1379 | -26.8966 | 214.7521 | -26.9133 | -26.9 | 1379 | 57.4583
| 1380 | -26.9133 | 214.4785 | -26.93 | -26.9 | 1380 | 57.5
| 1381 | -26.93 | 214.2053 | -26.9466 | -26.9 | 1381 | 57.5417
| 1382 | -26.9466 | 213.9324 | -26.9632 | -27 | 1382 | 57.5833
| 1383 | -26.9632 | 213.6598 | -26.9799 | -27 | 1383 | 57.625
| 1384 | -26.9799 | 213.3877 | -26.9964 | -27 | 1384 | 57.6667
| 1385 | -26.9964 | 213.1158 | -27.013 | -27 | 1385 | 57.7083
| 1386 | -27.013 | 212.8443 | -27.0296 | -27 | 1386 | 57.75
| 1387 | -27.0296 | 212.5732 | -27.0461 | -27 | 1387 | 57.7917
| 1388 | -27.0461 | 212.3024 | -27.0626 | -27.1 | 1388 | 57.8333
| 1389 | -27.0626 | 212.0319 | -27.0791 | -27.1 | 1389 | 57.875
| 1390 | -27.0791 | 211.7618 | -27.0955 | -27.1 | 1390 | 57.9167
| 1391 | -27.0955 | 211.492 | -27.112 | -27.1 | 1391 | 57.9583
| 1392 | -27.112 | 211.2226 | -27.1284 | -27.1 | 1392 | 58
| 1393 | -27.1284 | 210.9535 | -27.1448 | -27.1 | 1393 | 58.0417
| 1394 | -27.1448 | 210.6848 | -27.1612 | -27.2 | 1394 | 58.0833
| 1395 | -27.1612 | 210.4164 | -27.1775 | -27.2 | 1395 | 58.125
| 1396 | -27.1775 | 210.1483 | -27.1938 | -27.2 | 1396 | 58.1667
| 1397 | -27.1938 | 209.8806 | -27.2102 | -27.2 | 1397 | 58.2083
| 1398 | -27.2102 | 209.6133 | -27.2265 | -27.2 | 1398 | 58.25
| 1399 | -27.2265 | 209.3462 | -27.2427 | -27.2 | 1399 | 58.2917
| 1400 | -27.2427 | 209.0795 | -27.259 | -27.3 | 1400 | 58.3333
| 1401 | -27.259 | 208.8132 | -27.2752 | -27.3 | 1401 | 58.375
| 1402 | -27.2752 | 208.5472 | -27.2914 | -27.3 | 1402 | 58.4167
| 1403 | -27.2914 | 208.2815 | -27.3076 | -27.3 | 1403 | 58.4583
| 1404 | -27.3076 | 208.0162 | -27.3238 | -27.3 | 1404 | 58.5
| 1405 | -27.3238 | 207.7512 | -27.3399 | -27.3 | 1405 | 58.5417
| 1406 | -27.3399 | 207.4865 | -27.3561 | -27.4 | 1406 | 58.5833
| 1407 | -27.3561 | 207.2222 | -27.3722 | -27.4 | 1407 | 58.625
| 1408 | -27.3722 | 206.9582 | -27.3882 | -27.4 | 1408 | 58.6667
| 1409 | -27.3882 | 206.6945 | -27.4043 | -27.4 | 1409 | 58.7083
| 1410 | -27.4043 | 206.4312 | -27.4204 | -27.4 | 1410 | 58.75
| 1411 | -27.4204 | 206.1683 | -27.4364 | -27.4 | 1411 | 58.7917
| 1412 | -27.4364 | 205.9056 | -27.4524 | -27.5 | 1412 | 58.8333
| 1413 | -27.4524 | 205.6433 | -27.4684 | -27.5 | 1413 | 58.875
| 1414 | -27.4684 | 205.3813 | -27.4843 | -27.5 | 1414 | 58.9167
| 1415 | -27.4843 | 205.1197 | -27.5003 | -27.5 | 1415 | 58.9583
| 1416 | -27.5003 | 204.8584 | -27.5162 | -27.5 | 1416 | 59
| 1417 | -27.5162 | 204.5974 | -27.5321 | -27.5 | 1417 | 59.0417
| 1418 | -27.5321 | 204.3368 | -27.548 | -27.5 | 1418 | 59.0833
| 1419 | -27.548 | 204.0765 | -27.5639 | -27.6 | 1419 | 59.125
| 1420 | -27.5639 | 203.8165 | -27.5797 | -27.6 | 1420 | 59.1667
| 1421 | -27.5797 | 203.5568 | -27.5955 | -27.6 | 1421 | 59.2083
| 1422 | -27.5955 | 203.2975 | -27.6113 | -27.6 | 1422 | 59.25
| 1423 | -27.6113 | 203.0385 | -27.6271 | -27.6 | 1423 | 59.2917
| 1424 | -27.6271 | 202.7799 | -27.6429 | -27.6 | 1424 | 59.3333
| 1425 | -27.6429 | 202.5215 | -27.6586 | -27.7 | 1425 | 59.375
| 1426 | -27.6586 | 202.2635 | -27.6743 | -27.7 | 1426 | 59.4167
| 1427 | -27.6743 | 202.0059 | -27.69 | -27.7 | 1427 | 59.4583
| 1428 | -27.69 | 201.7485 | -27.7057 | -27.7 | 1428 | 59.5
| 1429 | -27.7057 | 201.4915 | -27.7214 | -27.7 | 1429 | 59.5417
| 1430 | -27.7214 | 201.2348 | -27.737 | -27.7 | 1430 | 59.5833
| 1431 | -27.737 | 200.9785 | -27.7526 | -27.8 | 1431 | 59.625
| 1432 | -27.7526 | 200.7225 | -27.7682 | -27.8 | 1432 | 59.6667
| 1433 | -27.7682 | 200.4667 | -27.7838 | -27.8 | 1433 | 59.7083
| 1434 | -27.7838 | 200.2114 | -27.7994 | -27.8 | 1434 | 59.75
| 1435 | -27.7994 | 199.9563 | -27.8149 | -27.8 | 1435 | 59.7917
| 1436 | -27.8149 | 199.7016 | -27.8305 | -27.8 | 1436 | 59.8333
| 1437 | -27.8305 | 199.4472 | -27.846 | -27.8 | 1437 | 59.875
| 1438 | -27.846 | 199.1931 | -27.8614 | -27.9 | 1438 | 59.9167
| 1439 | -27.8614 | 198.9393 | -27.8769 | -27.9 | 1439 | 59.9583
| 1440 | -27.8769 | 198.6859 | -27.8923 | -27.9 | 1440 | 60
| 1441 | -27.8923 | 198.4328 | -27.9078 | -27.9 | 1441 | 60.0417
| 1442 | -27.9078 | 198.18 | -27.9232 | -27.9 | 1442 | 60.0833
| 1443 | -27.9232 | 197.9275 | -27.9386 | -27.9 | 1443 | 60.125
| 1444 | -27.9386 | 197.6754 | -27.9539 | -28 | 1444 | 60.1667
| 1445 | -27.9539 | 197.4236 | -27.9693 | -28 | 1445 | 60.2083
| 1446 | -27.9693 | 197.1721 | -27.9846 | -28 | 1446 | 60.25
| 1447 | -27.9846 | 196.9209 | -27.9999 | -28 | 1447 | 60.2917
| 1448 | -27.9999 | 196.67 | -28.0152 | -28 | 1448 | 60.3333
| 1449 | -28.0152 | 196.4195 | -28.0305 | -28 | 1449 | 60.375
| 1450 | -28.0305 | 196.1693 | -28.0457 | -28 | 1450 | 60.4167
| 1451 | -28.0457 | 195.9194 | -28.0609 | -28.1 | 1451 | 60.4583
| 1452 | -28.0609 | 195.6698 | -28.0761 | -28.1 | 1452 | 60.5
| 1453 | -28.0761 | 195.4205 | -28.0913 | -28.1 | 1453 | 60.5417
| 1454 | -28.0913 | 195.1715 | -28.1065 | -28.1 | 1454 | 60.5833
| 1455 | -28.1065 | 194.9229 | -28.1217 | -28.1 | 1455 | 60.625
| 1456 | -28.1217 | 194.6746 | -28.1368 | -28.1 | 1456 | 60.6667
| 1457 | -28.1368 | 194.4266 | -28.1519 | -28.2 | 1457 | 60.7083
| 1458 | -28.1519 | 194.1789 | -28.167 | -28.2 | 1458 | 60.75
| 1459 | -28.167 | 193.9315 | -28.1821 | -28.2 | 1459 | 60.7917
| 1460 | -28.1821 | 193.6845 | -28.1971 | -28.2 | 1460 | 60.8333
| 1461 | -28.1971 | 193.4377 | -28.2122 | -28.2 | 1461 | 60.875
| 1462 | -28.2122 | 193.1913 | -28.2272 | -28.2 | 1462 | 60.9167
| 1463 | -28.2272 | 192.9452 | -28.2422 | -28.2 | 1463 | 60.9583
| 1464 | -28.2422 | 192.6994 | -28.2572 | -28.3 | 1464 | 61
| 1465 | -28.2572 | 192.4539 | -28.2721 | -28.3 | 1465 | 61.0417
| 1466 | -28.2721 | 192.2088 | -28.2871 | -28.3 | 1466 | 61.0833
| 1467 | -28.2871 | 191.9639 | -28.302 | -28.3 | 1467 | 61.125
| 1468 | -28.302 | 191.7194 | -28.3169 | -28.3 | 1468 | 61.1667
| 1469 | -28.3169 | 191.4751 | -28.3318 | -28.3 | 1469 | 61.2083
| 1470 | -28.3318 | 191.2312 | -28.3466 | -28.3 | 1470 | 61.25
| 1471 | -28.3466 | 190.9876 | -28.3615 | -28.4 | 1471 | 61.2917
| 1472 | -28.3615 | 190.7443 | -28.3763 | -28.4 | 1472 | 61.3333
| 1473 | -28.3763 | 190.5013 | -28.3911 | -28.4 | 1473 | 61.375
| 1474 | -28.3911 | 190.2586 | -28.4059 | -28.4 | 1474 | 61.4167
| 1475 | -28.4059 | 190.0162 | -28.4207 | -28.4 | 1475 | 61.4583
| 1476 | -28.4207 | 189.7742 | -28.4354 | -28.4 | 1476 | 61.5
| 1477 | -28.4354 | 189.5324 | -28.4502 | -28.5 | 1477 | 61.5417
| 1478 | -28.4502 | 189.2909 | -28.4649 | -28.5 | 1478 | 61.5833
| 1479 | -28.4649 | 189.0498 | -28.4796 | -28.5 | 1479 | 61.625
| 1480 | -28.4796 | 188.809 | -28.4942 | -28.5 | 1480 | 61.6667
| 1481 | -28.4942 | 188.5684 | -28.5089 | -28.5 | 1481 | 61.7083
| 1482 | -28.5089 | 188.3282 | -28.5235 | -28.5 | 1482 | 61.75
| 1483 | -28.5235 | 188.0883 | -28.5382 | -28.5 | 1483 | 61.7917
| 1484 | -28.5382 | 187.8487 | -28.5528 | -28.6 | 1484 | 61.8333
| 1485 | -28.5528 | 187.6094 | -28.5673 | -28.6 | 1485 | 61.875
| 1486 | -28.5673 | 187.3704 | -28.5819 | -28.6 | 1486 | 61.9167
| 1487 | -28.5819 | 187.1317 | -28.5964 | -28.6 | 1487 | 61.9583
| 1488 | -28.5964 | 186.8933 | -28.611 | -28.6 | 1488 | 62
| 1489 | -28.611 | 186.6552 | -28.6255 | -28.6 | 1489 | 62.0417
| 1490 | -28.6255 | 186.4174 | -28.64 | -28.6 | 1490 | 62.0833
| 1491 | -28.64 | 186.1799 | -28.6544 | -28.7 | 1491 | 62.125
| 1492 | -28.6544 | 185.9428 | -28.6689 | -28.7 | 1492 | 62.1667
| 1493 | -28.6689 | 185.7059 | -28.6833 | -28.7 | 1493 | 62.2083
| 1494 | -28.6833 | 185.4693 | -28.6977 | -28.7 | 1494 | 62.25
| 1495 | -28.6977 | 185.233 | -28.7121 | -28.7 | 1495 | 62.2917
| 1496 | -28.7121 | 184.9971 | -28.7265 | -28.7 | 1496 | 62.3333
| 1497 | -28.7265 | 184.7614 | -28.7409 | -28.7 | 1497 | 62.375
| 1498 | -28.7409 | 184.526 | -28.7552 | -28.8 | 1498 | 62.4167
| 1499 | -28.7552 | 184.2909 | -28.7696 | -28.8 | 1499 | 62.4583
| 1500 | -28.7696 | 184.0562 | -28.7839 | -28.8 | 1500 | 62.5
| 1501 | -28.7839 | 183.8217 | -28.7982 | -28.8 | 1501 | 62.5417
| 1502 | -28.7982 | 183.5875 | -28.8124 | -28.8 | 1502 | 62.5833
| 1503 | -28.8124 | 183.3537 | -28.8267 | -28.8 | 1503 | 62.625
| 1504 | -28.8267 | 183.1201 | -28.8409 | -28.8 | 1504 | 62.6667
| 1505 | -28.8409 | 182.8868 | -28.8551 | -28.9 | 1505 | 62.7083
| 1506 | -28.8551 | 182.6538 | -28.8693 | -28.9 | 1506 | 62.75
| 1507 | -28.8693 | 182.4211 | -28.8835 | -28.9 | 1507 | 62.7917
| 1508 | -28.8835 | 182.1887 | -28.8977 | -28.9 | 1508 | 62.8333
| 1509 | -28.8977 | 181.9566 | -28.9118 | -28.9 | 1509 | 62.875
| 1510 | -28.9118 | 181.7248 | -28.9259 | -28.9 | 1510 | 62.9167
| 1511 | -28.9259 | 181.4933 | -28.94 | -28.9 | 1511 | 62.9583
| 1512 | -28.94 | 181.2621 | -28.9541 | -29 | 1512 | 63
| 1513 | -28.9541 | 181.0312 | -28.9682 | -29 | 1513 | 63.0417
| 1514 | -28.9682 | 180.8006 | -28.9823 | -29 | 1514 | 63.0833
| 1515 | -28.9823 | 180.5703 | -28.9963 | -29 | 1515 | 63.125
| 1516 | -28.9963 | 180.3402 | -29.0103 | -29 | 1516 | 63.1667
| 1517 | -29.0103 | 180.1105 | -29.0243 | -29 | 1517 | 63.2083
| 1518 | -29.0243 | 179.881 | -29.0383 | -29 | 1518 | 63.25
| 1519 | -29.0383 | 179.6519 | -29.0523 | -29.1 | 1519 | 63.2917
| 1520 | -29.0523 | 179.423 | -29.0662 | -29.1 | 1520 | 63.3333
| 1521 | -29.0662 | 179.1945 | -29.0801 | -29.1 | 1521 | 63.375
| 1522 | -29.0801 | 178.9662 | -29.094 | -29.1 | 1522 | 63.4167
| 1523 | -29.094 | 178.7382 | -29.1079 | -29.1 | 1523 | 63.4583
| 1524 | -29.1079 | 178.5105 | -29.1218 | -29.1 | 1524 | 63.5
| 1525 | -29.1218 | 178.2831 | -29.1357 | -29.1 | 1525 | 63.5417
| 1526 | -29.1357 | 178.056 | -29.1495 | -29.1 | 1526 | 63.5833
| 1527 | -29.1495 | 177.8291 | -29.1633 | -29.2 | 1527 | 63.625
| 1528 | -29.1633 | 177.6026 | -29.1771 | -29.2 | 1528 | 63.6667
| 1529 | -29.1771 | 177.3763 | -29.1909 | -29.2 | 1529 | 63.7083
| 1530 | -29.1909 | 177.1504 | -29.2047 | -29.2 | 1530 | 63.75
| 1531 | -29.2047 | 176.9247 | -29.2184 | -29.2 | 1531 | 63.7917
| 1532 | -29.2184 | 176.6993 | -29.2322 | -29.2 | 1532 | 63.8333
| 1533 | -29.2322 | 176.4742 | -29.2459 | -29.2 | 1533 | 63.875
| 1534 | -29.2459 | 176.2494 | -29.2596 | -29.3 | 1534 | 63.9167
| 1535 | -29.2596 | 176.0249 | -29.2733 | -29.3 | 1535 | 63.9583
| 1536 | -29.2733 | 175.8006 | -29.2869 | -29.3 | 1536 | 64
| 1537 | -29.2869 | 175.5767 | -29.3006 | -29.3 | 1537 | 64.0417
| 1538 | -29.3006 | 175.353 | -29.3142 | -29.3 | 1538 | 64.0833
| 1539 | -29.3142 | 175.1296 | -29.3278 | -29.3 | 1539 | 64.125
| 1540 | -29.3278 | 174.9065 | -29.3414 | -29.3 | 1540 | 64.1667
| 1541 | -29.3414 | 174.6837 | -29.355 | -29.4 | 1541 | 64.2083
| 1542 | -29.355 | 174.4611 | -29.3686 | -29.4 | 1542 | 64.25
| 1543 | -29.3686 | 174.2389 | -29.3821 | -29.4 | 1543 | 64.2917
| 1544 | -29.3821 | 174.0169 | -29.3956 | -29.4 | 1544 | 64.3333
| 1545 | -29.3956 | 173.7952 | -29.4092 | -29.4 | 1545 | 64.375
| 1546 | -29.4092 | 173.5738 | -29.4226 | -29.4 | 1546 | 64.4167
| 1547 | -29.4226 | 173.3527 | -29.4361 | -29.4 | 1547 | 64.4583
| 1548 | -29.4361 | 173.1319 | -29.4496 | -29.4 | 1548 | 64.5
| 1549 | -29.4496 | 172.9113 | -29.463 | -29.5 | 1549 | 64.5417
| 1550 | -29.463 | 172.6911 | -29.4764 | -29.5 | 1550 | 64.5833
| 1551 | -29.4764 | 172.4711 | -29.4898 | -29.5 | 1551 | 64.625
| 1552 | -29.4898 | 172.2513 | -29.5032 | -29.5 | 1552 | 64.6667
| 1553 | -29.5032 | 172.0319 | -29.5166 | -29.5 | 1553 | 64.7083
| 1554 | -29.5166 | 171.8128 | -29.53 | -29.5 | 1554 | 64.75
| 1555 | -29.53 | 171.5939 | -29.5433 | -29.5 | 1555 | 64.7917
| 1556 | -29.5433 | 171.3753 | -29.5566 | -29.6 | 1556 | 64.8333
| 1557 | -29.5566 | 171.157 | -29.5699 | -29.6 | 1557 | 64.875
| 1558 | -29.5699 | 170.9389 | -29.5832 | -29.6 | 1558 | 64.9167
| 1559 | -29.5832 | 170.7212 | -29.5965 | -29.6 | 1559 | 64.9583
| 1560 | -29.5965 | 170.5037 | -29.6097 | -29.6 | 1560 | 65
| 1561 | -29.6097 | 170.2865 | -29.623 | -29.6 | 1561 | 65.0417
| 1562 | -29.623 | 170.0695 | -29.6362 | -29.6 | 1562 | 65.0833
| 1563 | -29.6362 | 169.8529 | -29.6494 | -29.6 | 1563 | 65.125
| 1564 | -29.6494 | 169.6365 | -29.6626 | -29.7 | 1564 | 65.1667
| 1565 | -29.6626 | 169.4204 | -29.6757 | -29.7 | 1565 | 65.2083
| 1566 | -29.6757 | 169.2046 | -29.6889 | -29.7 | 1566 | 65.25
| 1567 | -29.6889 | 168.989 | -29.702 | -29.7 | 1567 | 65.2917
| 1568 | -29.702 | 168.7737 | -29.7152 | -29.7 | 1568 | 65.3333
| 1569 | -29.7152 | 168.5587 | -29.7283 | -29.7 | 1569 | 65.375
| 1570 | -29.7283 | 168.344 | -29.7413 | -29.7 | 1570 | 65.4167
| 1571 | -29.7413 | 168.1295 | -29.7544 | -29.8 | 1571 | 65.4583
| 1572 | -29.7544 | 167.9153 | -29.7675 | -29.8 | 1572 | 65.5
| 1573 | -29.7675 | 167.7014 | -29.7805 | -29.8 | 1573 | 65.5417
| 1574 | -29.7805 | 167.4878 | -29.7935 | -29.8 | 1574 | 65.5833
| 1575 | -29.7935 | 167.2744 | -29.8065 | -29.8 | 1575 | 65.625
| 1576 | -29.8065 | 167.0613 | -29.8195 | -29.8 | 1576 | 65.6667
| 1577 | -29.8195 | 166.8485 | -29.8325 | -29.8 | 1577 | 65.7083
| 1578 | -29.8325 | 166.636 | -29.8454 | -29.8 | 1578 | 65.75
| 1579 | -29.8454 | 166.4237 | -29.8584 | -29.9 | 1579 | 65.7917
| 1580 | -29.8584 | 166.2117 | -29.8713 | -29.9 | 1580 | 65.8333
| 1581 | -29.8713 | 165.9999 | -29.8842 | -29.9 | 1581 | 65.875
| 1582 | -29.8842 | 165.7885 | -29.8971 | -29.9 | 1582 | 65.9167
| 1583 | -29.8971 | 165.5773 | -29.9099 | -29.9 | 1583 | 65.9583
| 1584 | -29.9099 | 165.3663 | -29.9228 | -29.9 | 1584 | 66
| 1585 | -29.9228 | 165.1557 | -29.9356 | -29.9 | 1585 | 66.0417
| 1586 | -29.9356 | 164.9453 | -29.9485 | -29.9 | 1586 | 66.0833
| 1587 | -29.9485 | 164.7351 | -29.9613 | -30 | 1587 | 66.125
| 1588 | -29.9613 | 164.5253 | -29.9741 | -30 | 1588 | 66.1667
| 1589 | -29.9741 | 164.3157 | -29.9868 | -30 | 1589 | 66.2083
| 1590 | -29.9868 | 164.1064 | -29.9996 | -30 | 1590 | 66.25
| 1591 | -29.9996 | 163.8973 | -30.0123 | -30 | 1591 | 66.2917
| 1592 | -30.0123 | 163.6885 | -30.025 | -30 | 1592 | 66.3333
| 1593 | -30.025 | 163.48 | -30.0378 | -30 | 1593 | 66.375
| 1594 | -30.0378 | 163.2717 | -30.0504 | -30.1 | 1594 | 66.4167
| 1595 | -30.0504 | 163.0637 | -30.0631 | -30.1 | 1595 | 66.4583
| 1596 | -30.0631 | 162.856 | -30.0758 | -30.1 | 1596 | 66.5
| 1597 | -30.0758 | 162.6485 | -30.0884 | -30.1 | 1597 | 66.5417
| 1598 | -30.0884 | 162.4413 | -30.101 | -30.1 | 1598 | 66.5833
| 1599 | -30.101 | 162.2344 | -30.1137 | -30.1 | 1599 | 66.625
| 1600 | -30.1137 | 162.0277 | -30.1262 | -30.1 | 1600 | 66.6667
| 1601 | -30.1262 | 161.8213 | -30.1388 | -30.1 | 1601 | 66.7083
| 1602 | -30.1388 | 161.6151 | -30.1514 | -30.2 | 1602 | 66.75
| 1603 | -30.1514 | 161.4093 | -30.1639 | -30.2 | 1603 | 66.7917
| 1604 | -30.1639 | 161.2036 | -30.1765 | -30.2 | 1604 | 66.8333
| 1605 | -30.1765 | 160.9983 | -30.189 | -30.2 | 1605 | 66.875
| 1606 | -30.189 | 160.7932 | -30.2015 | -30.2 | 1606 | 66.9167
| 1607 | -30.2015 | 160.5883 | -30.214 | -30.2 | 1607 | 66.9583
| 1608 | -30.214 | 160.3838 | -30.2264 | -30.2 | 1608 | 67
| 1609 | -30.2264 | 160.1794 | -30.2389 | -30.2 | 1609 | 67.0417
| 1610 | -30.2389 | 159.9754 | -30.2513 | -30.3 | 1610 | 67.0833
| 1611 | -30.2513 | 159.7716 | -30.2637 | -30.3 | 1611 | 67.125
| 1612 | -30.2637 | 159.5681 | -30.2761 | -30.3 | 1612 | 67.1667
| 1613 | -30.2761 | 159.3648 | -30.2885 | -30.3 | 1613 | 67.2083
| 1614 | -30.2885 | 159.1618 | -30.3009 | -30.3 | 1614 | 67.25
| 1615 | -30.3009 | 158.959 | -30.3133 | -30.3 | 1615 | 67.2917
| 1616 | -30.3133 | 158.7565 | -30.3256 | -30.3 | 1616 | 67.3333
| 1617 | -30.3256 | 158.5543 | -30.3379 | -30.3 | 1617 | 67.375
| 1618 | -30.3379 | 158.3523 | -30.3502 | -30.4 | 1618 | 67.4167
| 1619 | -30.3502 | 158.1505 | -30.3625 | -30.4 | 1619 | 67.4583
| 1620 | -30.3625 | 157.9491 | -30.3748 | -30.4 | 1620 | 67.5
| 1621 | -30.3748 | 157.7478 | -30.3871 | -30.4 | 1621 | 67.5417
| 1622 | -30.3871 | 157.5469 | -30.3993 | -30.4 | 1622 | 67.5833
| 1623 | -30.3993 | 157.3462 | -30.4115 | -30.4 | 1623 | 67.625
| 1624 | -30.4115 | 157.1457 | -30.4238 | -30.4 | 1624 | 67.6667
| 1625 | -30.4238 | 156.9455 | -30.4359 | -30.4 | 1625 | 67.7083
| 1626 | -30.4359 | 156.7456 | -30.4481 | -30.4 | 1626 | 67.75
| 1627 | -30.4481 | 156.5459 | -30.4603 | -30.5 | 1627 | 67.7917
| 1628 | -30.4603 | 156.3465 | -30.4725 | -30.5 | 1628 | 67.8333
| 1629 | -30.4725 | 156.1473 | -30.4846 | -30.5 | 1629 | 67.875
| 1630 | -30.4846 | 155.9484 | -30.4967 | -30.5 | 1630 | 67.9167
| 1631 | -30.4967 | 155.7497 | -30.5088 | -30.5 | 1631 | 67.9583
| 1632 | -30.5088 | 155.5513 | -30.5209 | -30.5 | 1632 | 68
| 1633 | -30.5209 | 155.3532 | -30.533 | -30.5 | 1633 | 68.0417
| 1634 | -30.533 | 155.1553 | -30.545 | -30.5 | 1634 | 68.0833
| 1635 | -30.545 | 154.9576 | -30.5571 | -30.6 | 1635 | 68.125
| 1636 | -30.5571 | 154.7602 | -30.5691 | -30.6 | 1636 | 68.1667
| 1637 | -30.5691 | 154.563 | -30.5811 | -30.6 | 1637 | 68.2083
| 1638 | -30.5811 | 154.3661 | -30.5931 | -30.6 | 1638 | 68.25
| 1639 | -30.5931 | 154.1695 | -30.6051 | -30.6 | 1639 | 68.2917
| 1640 | -30.6051 | 153.9731 | -30.6171 | -30.6 | 1640 | 68.3333
| 1641 | -30.6171 | 153.7769 | -30.629 | -30.6 | 1641 | 68.375
| 1642 | -30.629 | 153.581 | -30.641 | -30.6 | 1642 | 68.4167
| 1643 | -30.641 | 153.3854 | -30.6529 | -30.7 | 1643 | 68.4583
| 1644 | -30.6529 | 153.19 | -30.6648 | -30.7 | 1644 | 68.5
| 1645 | -30.6648 | 152.9948 | -30.6767 | -30.7 | 1645 | 68.5417
| 1646 | -30.6767 | 152.7999 | -30.6886 | -30.7 | 1646 | 68.5833
| 1647 | -30.6886 | 152.6053 | -30.7004 | -30.7 | 1647 | 68.625
| 1648 | -30.7004 | 152.4109 | -30.7123 | -30.7 | 1648 | 68.6667
| 1649 | -30.7123 | 152.2167 | -30.7241 | -30.7 | 1649 | 68.7083
| 1650 | -30.7241 | 152.0228 | -30.7359 | -30.7 | 1650 | 68.75
| 1651 | -30.7359 | 151.8291 | -30.7477 | -30.7 | 1651 | 68.7917
| 1652 | -30.7477 | 151.6357 | -30.7595 | -30.8 | 1652 | 68.8333
| 1653 | -30.7595 | 151.4425 | -30.7713 | -30.8 | 1653 | 68.875
| 1654 | -30.7713 | 151.2496 | -30.7831 | -30.8 | 1654 | 68.9167
| 1655 | -30.7831 | 151.0569 | -30.7948 | -30.8 | 1655 | 68.9583
| 1656 | -30.7948 | 150.8645 | -30.8065 | -30.8 | 1656 | 69
| 1657 | -30.8065 | 150.6723 | -30.8182 | -30.8 | 1657 | 69.0417
| 1658 | -30.8182 | 150.4804 | -30.8299 | -30.8 | 1658 | 69.0833
| 1659 | -30.8299 | 150.2887 | -30.8416 | -30.8 | 1659 | 69.125
| 1660 | -30.8416 | 150.0972 | -30.8533 | -30.9 | 1660 | 69.1667
| 1661 | -30.8533 | 149.906 | -30.8649 | -30.9 | 1661 | 69.2083
| 1662 | -30.8649 | 149.715 | -30.8766 | -30.9 | 1662 | 69.25
| 1663 | -30.8766 | 149.5243 | -30.8882 | -30.9 | 1663 | 69.2917
| 1664 | -30.8882 | 149.3338 | -30.8998 | -30.9 | 1664 | 69.3333
| 1665 | -30.8998 | 149.1436 | -30.9114 | -30.9 | 1665 | 69.375
| 1666 | -30.9114 | 148.9536 | -30.923 | -30.9 | 1666 | 69.4167
| 1667 | -30.923 | 148.7638 | -30.9345 | -30.9 | 1667 | 69.4583
| 1668 | -30.9345 | 148.5743 | -30.9461 | -30.9 | 1668 | 69.5
| 1669 | -30.9461 | 148.385 | -30.9576 | -31 | 1669 | 69.5417
| 1670 | -30.9576 | 148.196 | -30.9691 | -31 | 1670 | 69.5833
| 1671 | -30.9691 | 148.0072 | -30.9806 | -31 | 1671 | 69.625
| 1672 | -30.9806 | 147.8187 | -30.9921 | -31 | 1672 | 69.6667
| 1673 | -30.9921 | 147.6304 | -31.0036 | -31 | 1673 | 69.7083
| 1674 | -31.0036 | 147.4423 | -31.0151 | -31 | 1674 | 69.75
| 1675 | -31.0151 | 147.2545 | -31.0265 | -31 | 1675 | 69.7917
| 1676 | -31.0265 | 147.0669 | -31.0379 | -31 | 1676 | 69.8333
| 1677 | -31.0379 | 146.8795 | -31.0494 | -31 | 1677 | 69.875
| 1678 | -31.0494 | 146.6924 | -31.0608 | -31.1 | 1678 | 69.9167
| 1679 | -31.0608 | 146.5055 | -31.0722 | -31.1 | 1679 | 69.9583
| 1680 | -31.0722 | 146.3189 | -31.0835 | -31.1 | 1680 | 70
| 1681 | -31.0835 | 146.1325 | -31.0949 | -31.1 | 1681 | 70.0417
| 1682 | -31.0949 | 145.9463 | -31.1062 | -31.1 | 1682 | 70.0833
| 1683 | -31.1062 | 145.7604 | -31.1176 | -31.1 | 1683 | 70.125
| 1684 | -31.1176 | 145.5747 | -31.1289 | -31.1 | 1684 | 70.1667
| 1685 | -31.1289 | 145.3893 | -31.1402 | -31.1 | 1685 | 70.2083
| 1686 | -31.1402 | 145.204 | -31.1515 | -31.2 | 1686 | 70.25
| 1687 | -31.1515 | 145.0191 | -31.1627 | -31.2 | 1687 | 70.2917
| 1688 | -31.1627 | 144.8343 | -31.174 | -31.2 | 1688 | 70.3333
| 1689 | -31.174 | 144.6498 | -31.1852 | -31.2 | 1689 | 70.375
| 1690 | -31.1852 | 144.4655 | -31.1965 | -31.2 | 1690 | 70.4167
| 1691 | -31.1965 | 144.2815 | -31.2077 | -31.2 | 1691 | 70.4583
| 1692 | -31.2077 | 144.0977 | -31.2189 | -31.2 | 1692 | 70.5
| 1693 | -31.2189 | 143.9141 | -31.2301 | -31.2 | 1693 | 70.5417
| 1694 | -31.2301 | 143.7308 | -31.2412 | -31.2 | 1694 | 70.5833
| 1695 | -31.2412 | 143.5477 | -31.2524 | -31.3 | 1695 | 70.625
| 1696 | -31.2524 | 143.3648 | -31.2635 | -31.3 | 1696 | 70.6667
| 1697 | -31.2635 | 143.1822 | -31.2747 | -31.3 | 1697 | 70.7083
| 1698 | -31.2747 | 142.9998 | -31.2858 | -31.3 | 1698 | 70.75
| 1699 | -31.2858 | 142.8176 | -31.2969 | -31.3 | 1699 | 70.7917
| 1700 | -31.2969 | 142.6357 | -31.308 | -31.3 | 1700 | 70.8333
| 1701 | -31.308 | 142.454 | -31.319 | -31.3 | 1701 | 70.875
| 1702 | -31.319 | 142.2725 | -31.3301 | -31.3 | 1702 | 70.9167
| 1703 | -31.3301 | 142.0912 | -31.3412 | -31.3 | 1703 | 70.9583
| 1704 | -31.3412 | 141.9102 | -31.3522 | -31.4 | 1704 | 71
| 1705 | -31.3522 | 141.7295 | -31.3632 | -31.4 | 1705 | 71.0417
| 1706 | -31.3632 | 141.5489 | -31.3742 | -31.4 | 1706 | 71.0833
| 1707 | -31.3742 | 141.3686 | -31.3852 | -31.4 | 1707 | 71.125
| 1708 | -31.3852 | 141.1885 | -31.3962 | -31.4 | 1708 | 71.1667
| 1709 | -31.3962 | 141.0086 | -31.4071 | -31.4 | 1709 | 71.2083
| 1710 | -31.4071 | 140.829 | -31.4181 | -31.4 | 1710 | 71.25
| 1711 | -31.4181 | 140.6496 | -31.429 | -31.4 | 1711 | 71.2917
| 1712 | -31.429 | 140.4704 | -31.4399 | -31.4 | 1712 | 71.3333
| 1713 | -31.4399 | 140.2915 | -31.4508 | -31.5 | 1713 | 71.375
| 1714 | -31.4508 | 140.1127 | -31.4617 | -31.5 | 1714 | 71.4167
| 1715 | -31.4617 | 139.9342 | -31.4726 | -31.5 | 1715 | 71.4583
| 1716 | -31.4726 | 139.756 | -31.4835 | -31.5 | 1716 | 71.5
| 1717 | -31.4835 | 139.5779 | -31.4943 | -31.5 | 1717 | 71.5417
| 1718 | -31.4943 | 139.4001 | -31.5051 | -31.5 | 1718 | 71.5833
| 1719 | -31.5051 | 139.2225 | -31.516 | -31.5 | 1719 | 71.625
| 1720 | -31.516 | 139.0452 | -31.5268 | -31.5 | 1720 | 71.6667
| 1721 | -31.5268 | 138.868 | -31.5376 | -31.5 | 1721 | 71.7083
| 1722 | -31.5376 | 138.6911 | -31.5483 | -31.5 | 1722 | 71.75
| 1723 | -31.5483 | 138.5145 | -31.5591 | -31.6 | 1723 | 71.7917
| 1724 | -31.5591 | 138.338 | -31.5699 | -31.6 | 1724 | 71.8333
| 1725 | -31.5699 | 138.1618 | -31.5806 | -31.6 | 1725 | 71.875
| 1726 | -31.5806 | 137.9858 | -31.5913 | -31.6 | 1726 | 71.9167
| 1727 | -31.5913 | 137.81 | -31.602 | -31.6 | 1727 | 71.9583
| 1728 | -31.602 | 137.6344 | -31.6127 | -31.6 | 1728 | 72
| 1729 | -31.6127 | 137.4591 | -31.6234 | -31.6 | 1729 | 72.0417
| 1730 | -31.6234 | 137.284 | -31.6341 | -31.6 | 1730 | 72.0833
| 1731 | -31.6341 | 137.1091 | -31.6448 | -31.6 | 1731 | 72.125
| 1732 | -31.6448 | 136.9344 | -31.6554 | -31.7 | 1732 | 72.1667
| 1733 | -31.6554 | 136.76 | -31.666 | -31.7 | 1733 | 72.2083
| 1734 | -31.666 | 136.5857 | -31.6766 | -31.7 | 1734 | 72.25
| 1735 | -31.6766 | 136.4117 | -31.6873 | -31.7 | 1735 | 72.2917
| 1736 | -31.6873 | 136.238 | -31.6978 | -31.7 | 1736 | 72.3333
| 1737 | -31.6978 | 136.0644 | -31.7084 | -31.7 | 1737 | 72.375
| 1738 | -31.7084 | 135.8911 | -31.719 | -31.7 | 1738 | 72.4167
| 1739 | -31.719 | 135.718 | -31.7295 | -31.7 | 1739 | 72.4583
| 1740 | -31.7295 | 135.5451 | -31.7401 | -31.7 | 1740 | 72.5
| 1741 | -31.7401 | 135.3724 | -31.7506 | -31.8 | 1741 | 72.5417
| 1742 | -31.7506 | 135.1999 | -31.7611 | -31.8 | 1742 | 72.5833
| 1743 | -31.7611 | 135.0277 | -31.7716 | -31.8 | 1743 | 72.625
| 1744 | -31.7716 | 134.8557 | -31.7821 | -31.8 | 1744 | 72.6667
| 1745 | -31.7821 | 134.6839 | -31.7925 | -31.8 | 1745 | 72.7083
| 1746 | -31.7925 | 134.5123 | -31.803 | -31.8 | 1746 | 72.75
| 1747 | -31.803 | 134.341 | -31.8134 | -31.8 | 1747 | 72.7917
| 1748 | -31.8134 | 134.1698 | -31.8239 | -31.8 | 1748 | 72.8333
| 1749 | -31.8239 | 133.9989 | -31.8343 | -31.8 | 1749 | 72.875
| 1750 | -31.8343 | 133.8282 | -31.8447 | -31.8 | 1750 | 72.9167
| 1751 | -31.8447 | 133.6577 | -31.8551 | -31.9 | 1751 | 72.9583
| 1752 | -31.8551 | 133.4874 | -31.8655 | -31.9 | 1752 | 73
| 1753 | -31.8655 | 133.3174 | -31.8758 | -31.9 | 1753 | 73.0417
| 1754 | -31.8758 | 133.1475 | -31.8862 | -31.9 | 1754 | 73.0833
| 1755 | -31.8862 | 132.9779 | -31.8965 | -31.9 | 1755 | 73.125
| 1756 | -31.8965 | 132.8085 | -31.9068 | -31.9 | 1756 | 73.1667
| 1757 | -31.9068 | 132.6393 | -31.9171 | -31.9 | 1757 | 73.2083
| 1758 | -31.9171 | 132.4704 | -31.9274 | -31.9 | 1758 | 73.25
| 1759 | -31.9274 | 132.3016 | -31.9377 | -31.9 | 1759 | 73.2917
| 1760 | -31.9377 | 132.1331 | -31.948 | -31.9 | 1760 | 73.3333
| 1761 | -31.948 | 131.9647 | -31.9582 | -32 | 1761 | 73.375
| 1762 | -31.9582 | 131.7966 | -31.9685 | -32 | 1762 | 73.4167
| 1763 | -31.9685 | 131.6287 | -31.9787 | -32 | 1763 | 73.4583
| 1764 | -31.9787 | 131.461 | -31.9889 | -32 | 1764 | 73.5
| 1765 | -31.9889 | 131.2936 | -31.9991 | -32 | 1765 | 73.5417
| 1766 | -31.9991 | 131.1263 | -32.0093 | -32 | 1766 | 73.5833
| 1767 | -32.0093 | 130.9593 | -32.0195 | -32 | 1767 | 73.625
| 1768 | -32.0195 | 130.7924 | -32.0297 | -32 | 1768 | 73.6667
| 1769 | -32.0297 | 130.6258 | -32.0398 | -32 | 1769 | 73.7083
| 1770 | -32.0398 | 130.4594 | -32.05 | -32 | 1770 | 73.75
| 1771 | -32.05 | 130.2932 | -32.0601 | -32.1 | 1771 | 73.7917
| 1772 | -32.0601 | 130.1272 | -32.0702 | -32.1 | 1772 | 73.8333
| 1773 | -32.0702 | 129.9615 | -32.0803 | -32.1 | 1773 | 73.875
| 1774 | -32.0803 | 129.7959 | -32.0904 | -32.1 | 1774 | 73.9167
| 1775 | -32.0904 | 129.6305 | -32.1005 | -32.1 | 1775 | 73.9583
| 1776 | -32.1005 | 129.4654 | -32.1106 | -32.1 | 1776 | 74
| 1777 | -32.1106 | 129.3005 | -32.1206 | -32.1 | 1777 | 74.0417
| 1778 | -32.1206 | 129.1358 | -32.1306 | -32.1 | 1778 | 74.0833
| 1779 | -32.1306 | 128.9712 | -32.1407 | -32.1 | 1779 | 74.125
| 1780 | -32.1407 | 128.8069 | -32.1507 | -32.2 | 1780 | 74.1667
| 1781 | -32.1507 | 128.6429 | -32.1607 | -32.2 | 1781 | 74.2083
| 1782 | -32.1607 | 128.479 | -32.1707 | -32.2 | 1782 | 74.25
| 1783 | -32.1707 | 128.3153 | -32.1806 | -32.2 | 1783 | 74.2917
| 1784 | -32.1806 | 128.1518 | -32.1906 | -32.2 | 1784 | 74.3333
| 1785 | -32.1906 | 127.9886 | -32.2005 | -32.2 | 1785 | 74.375
| 1786 | -32.2005 | 127.8255 | -32.2105 | -32.2 | 1786 | 74.4167
| 1787 | -32.2105 | 127.6627 | -32.2204 | -32.2 | 1787 | 74.4583
| 1788 | -32.2204 | 127.5001 | -32.2303 | -32.2 | 1788 | 74.5
| 1789 | -32.2303 | 127.3376 | -32.2402 | -32.2 | 1789 | 74.5417
| 1790 | -32.2402 | 127.1754 | -32.2501 | -32.3 | 1790 | 74.5833
| 1791 | -32.2501 | 127.0134 | -32.26 | -32.3 | 1791 | 74.625
| 1792 | -32.26 | 126.8516 | -32.2698 | -32.3 | 1792 | 74.6667
| 1793 | -32.2698 | 126.69 | -32.2797 | -32.3 | 1793 | 74.7083
| 1794 | -32.2797 | 126.5286 | -32.2895 | -32.3 | 1794 | 74.75
| 1795 | -32.2895 | 126.3674 | -32.2993 | -32.3 | 1795 | 74.7917
| 1796 | -32.2993 | 126.2064 | -32.3091 | -32.3 | 1796 | 74.8333
| 1797 | -32.3091 | 126.0457 | -32.3189 | -32.3 | 1797 | 74.875
| 1798 | -32.3189 | 125.8851 | -32.3287 | -32.3 | 1798 | 74.9167
| 1799 | -32.3287 | 125.7247 | -32.3385 | -32.3 | 1799 | 74.9583
| 1800 | -32.3385 | 125.5646 | -32.3483 | -32.3 | 1800 | 75
| 1801 | -32.3483 | 125.4046 | -32.358 | -32.4 | 1801 | 75.0417
| 1802 | -32.358 | 125.2448 | -32.3677 | -32.4 | 1802 | 75.0833
| 1803 | -32.3677 | 125.0853 | -32.3775 | -32.4 | 1803 | 75.125
| 1804 | -32.3775 | 124.9259 | -32.3872 | -32.4 | 1804 | 75.1667
| 1805 | -32.3872 | 124.7668 | -32.3969 | -32.4 | 1805 | 75.2083
| 1806 | -32.3969 | 124.6078 | -32.4066 | -32.4 | 1806 | 75.25
| 1807 | -32.4066 | 124.4491 | -32.4162 | -32.4 | 1807 | 75.2917
| 1808 | -32.4162 | 124.2906 | -32.4259 | -32.4 | 1808 | 75.3333
| 1809 | -32.4259 | 124.1322 | -32.4355 | -32.4 | 1809 | 75.375
| 1810 | -32.4355 | 123.9741 | -32.4452 | -32.4 | 1810 | 75.4167
| 1811 | -32.4452 | 123.8162 | -32.4548 | -32.5 | 1811 | 75.4583
| 1812 | -32.4548 | 123.6584 | -32.4644 | -32.5 | 1812 | 75.5
| 1813 | -32.4644 | 123.5009 | -32.474 | -32.5 | 1813 | 75.5417
| 1814 | -32.474 | 123.3436 | -32.4836 | -32.5 | 1814 | 75.5833
| 1815 | -32.4836 | 123.1864 | -32.4932 | -32.5 | 1815 | 75.625
| 1816 | -32.4932 | 123.0295 | -32.5027 | -32.5 | 1816 | 75.6667
| 1817 | -32.5027 | 122.8728 | -32.5123 | -32.5 | 1817 | 75.7083
| 1818 | -32.5123 | 122.7162 | -32.5218 | -32.5 | 1818 | 75.75
| 1819 | -32.5218 | 122.5599 | -32.5314 | -32.5 | 1819 | 75.7917
| 1820 | -32.5314 | 122.4038 | -32.5409 | -32.5 | 1820 | 75.8333
| 1821 | -32.5409 | 122.2478 | -32.5504 | -32.6 | 1821 | 75.875
| 1822 | -32.5504 | 122.0921 | -32.5599 | -32.6 | 1822 | 75.9167
| 1823 | -32.5599 | 121.9366 | -32.5693 | -32.6 | 1823 | 75.9583
| 1824 | -32.5693 | 121.7812 | -32.5788 | -32.6 | 1824 | 76
| 1825 | -32.5788 | 121.6261 | -32.5883 | -32.6 | 1825 | 76.0417
| 1826 | -32.5883 | 121.4712 | -32.5977 | -32.6 | 1826 | 76.0833
| 1827 | -32.5977 | 121.3164 | -32.6071 | -32.6 | 1827 | 76.125
| 1828 | -32.6071 | 121.1619 | -32.6166 | -32.6 | 1828 | 76.1667
| 1829 | -32.6166 | 121.0075 | -32.626 | -32.6 | 1829 | 76.2083
| 1830 | -32.626 | 120.8534 | -32.6354 | -32.6 | 1830 | 76.25
| 1831 | -32.6354 | 120.6994 | -32.6447 | -32.6 | 1831 | 76.2917
| 1832 | -32.6447 | 120.5456 | -32.6541 | -32.7 | 1832 | 76.3333
| 1833 | -32.6541 | 120.3921 | -32.6635 | -32.7 | 1833 | 76.375
| 1834 | -32.6635 | 120.2387 | -32.6728 | -32.7 | 1834 | 76.4167
| 1835 | -32.6728 | 120.0855 | -32.6821 | -32.7 | 1835 | 76.4583
| 1836 | -32.6821 | 119.9325 | -32.6915 | -32.7 | 1836 | 76.5
| 1837 | -32.6915 | 119.7798 | -32.7008 | -32.7 | 1837 | 76.5417
| 1838 | -32.7008 | 119.6272 | -32.7101 | -32.7 | 1838 | 76.5833
| 1839 | -32.7101 | 119.4748 | -32.7194 | -32.7 | 1839 | 76.625
| 1840 | -32.7194 | 119.3226 | -32.7286 | -32.7 | 1840 | 76.6667
| 1841 | -32.7286 | 119.1706 | -32.7379 | -32.7 | 1841 | 76.7083
| 1842 | -32.7379 | 119.0187 | -32.7472 | -32.7 | 1842 | 76.75
| 1843 | -32.7472 | 118.8671 | -32.7564 | -32.8 | 1843 | 76.7917
| 1844 | -32.7564 | 118.7157 | -32.7656 | -32.8 | 1844 | 76.8333
| 1845 | -32.7656 | 118.5645 | -32.7748 | -32.8 | 1845 | 76.875
| 1846 | -32.7748 | 118.4134 | -32.784 | -32.8 | 1846 | 76.9167
| 1847 | -32.784 | 118.2626 | -32.7932 | -32.8 | 1847 | 76.9583
| 1848 | -32.7932 | 118.1119 | -32.8024 | -32.8 | 1848 | 77
| 1849 | -32.8024 | 117.9615 | -32.8116 | -32.8 | 1849 | 77.0417
| 1850 | -32.8116 | 117.8112 | -32.8207 | -32.8 | 1850 | 77.0833
| 1851 | -32.8207 | 117.6611 | -32.8299 | -32.8 | 1851 | 77.125
| 1852 | -32.8299 | 117.5112 | -32.839 | -32.8 | 1852 | 77.1667
| 1853 | -32.839 | 117.3615 | -32.8481 | -32.8 | 1853 | 77.2083
| 1854 | -32.8481 | 117.212 | -32.8573 | -32.9 | 1854 | 77.25
| 1855 | -32.8573 | 117.0627 | -32.8664 | -32.9 | 1855 | 77.2917
| 1856 | -32.8664 | 116.9135 | -32.8754 | -32.9 | 1856 | 77.3333
| 1857 | -32.8754 | 116.7646 | -32.8845 | -32.9 | 1857 | 77.375
| 1858 | -32.8845 | 116.6159 | -32.8936 | -32.9 | 1858 | 77.4167
| 1859 | -32.8936 | 116.4673 | -32.9026 | -32.9 | 1859 | 77.4583
| 1860 | -32.9026 | 116.3189 | -32.9117 | -32.9 | 1860 | 77.5
| 1861 | -32.9117 | 116.1707 | -32.9207 | -32.9 | 1861 | 77.5417
| 1862 | -32.9207 | 116.0228 | -32.9297 | -32.9 | 1862 | 77.5833
| 1863 | -32.9297 | 115.8749 | -32.9387 | -32.9 | 1863 | 77.625
| 1864 | -32.9387 | 115.7273 | -32.9477 | -32.9 | 1864 | 77.6667
| 1865 | -32.9477 | 115.5799 | -32.9567 | -33 | 1865 | 77.7083
| 1866 | -32.9567 | 115.4327 | -32.9657 | -33 | 1866 | 77.75
| 1867 | -32.9657 | 115.2856 | -32.9747 | -33 | 1867 | 77.7917
| 1868 | -32.9747 | 115.1387 | -32.9836 | -33 | 1868 | 77.8333
| 1869 | -32.9836 | 114.9921 | -32.9925 | -33 | 1869 | 77.875
| 1870 | -32.9925 | 114.8456 | -33.0015 | -33 | 1870 | 77.9167
| 1871 | -33.0015 | 114.6993 | -33.0104 | -33 | 1871 | 77.9583
| 1872 | -33.0104 | 114.5532 | -33.0193 | -33 | 1872 | 78
| 1873 | -33.0193 | 114.4072 | -33.0282 | -33 | 1873 | 78.0417
| 1874 | -33.0282 | 114.2615 | -33.0371 | -33 | 1874 | 78.0833
| 1875 | -33.0371 | 114.1159 | -33.0459 | -33 | 1875 | 78.125
| 1876 | -33.0459 | 113.9705 | -33.0548 | -33.1 | 1876 | 78.1667
| 1877 | -33.0548 | 113.8253 | -33.0636 | -33.1 | 1877 | 78.2083
| 1878 | -33.0636 | 113.6803 | -33.0725 | -33.1 | 1878 | 78.25
| 1879 | -33.0725 | 113.5355 | -33.0813 | -33.1 | 1879 | 78.2917
| 1880 | -33.0813 | 113.3909 | -33.0901 | -33.1 | 1880 | 78.3333
| 1881 | -33.0901 | 113.2464 | -33.0989 | -33.1 | 1881 | 78.375
| 1882 | -33.0989 | 113.1022 | -33.1077 | -33.1 | 1882 | 78.4167
| 1883 | -33.1077 | 112.9581 | -33.1165 | -33.1 | 1883 | 78.4583
| 1884 | -33.1165 | 112.8142 | -33.1253 | -33.1 | 1884 | 78.5
| 1885 | -33.1253 | 112.6705 | -33.134 | -33.1 | 1885 | 78.5417
| 1886 | -33.134 | 112.5269 | -33.1428 | -33.1 | 1886 | 78.5833
| 1887 | -33.1428 | 112.3836 | -33.1515 | -33.2 | 1887 | 78.625
| 1888 | -33.1515 | 112.2404 | -33.1602 | -33.2 | 1888 | 78.6667
| 1889 | -33.1602 | 112.0974 | -33.1689 | -33.2 | 1889 | 78.7083
| 1890 | -33.1689 | 111.9546 | -33.1776 | -33.2 | 1890 | 78.75
| 1891 | -33.1776 | 111.812 | -33.1863 | -33.2 | 1891 | 78.7917
| 1892 | -33.1863 | 111.6696 | -33.195 | -33.2 | 1892 | 78.8333
| 1893 | -33.195 | 111.5273 | -33.2037 | -33.2 | 1893 | 78.875
| 1894 | -33.2037 | 111.3852 | -33.2123 | -33.2 | 1894 | 78.9167
| 1895 | -33.2123 | 111.2433 | -33.221 | -33.2 | 1895 | 78.9583
| 1896 | -33.221 | 111.1016 | -33.2296 | -33.2 | 1896 | 79
| 1897 | -33.2296 | 110.9601 | -33.2382 | -33.2 | 1897 | 79.0417
| 1898 | -33.2382 | 110.8187 | -33.2469 | -33.2 | 1898 | 79.0833
| 1899 | -33.2469 | 110.6776 | -33.2555 | -33.3 | 1899 | 79.125
| 1900 | -33.2555 | 110.5366 | -33.2641 | -33.3 | 1900 | 79.1667
| 1901 | -33.2641 | 110.3957 | -33.2726 | -33.3 | 1901 | 79.2083
| 1902 | -33.2726 | 110.2551 | -33.2812 | -33.3 | 1902 | 79.25
| 1903 | -33.2812 | 110.1146 | -33.2898 | -33.3 | 1903 | 79.2917
| 1904 | -33.2898 | 109.9744 | -33.2983 | -33.3 | 1904 | 79.3333
| 1905 | -33.2983 | 109.8343 | -33.3068 | -33.3 | 1905 | 79.375
| 1906 | -33.3068 | 109.6944 | -33.3154 | -33.3 | 1906 | 79.4167
| 1907 | -33.3154 | 109.5546 | -33.3239 | -33.3 | 1907 | 79.4583
| 1908 | -33.3239 | 109.415 | -33.3324 | -33.3 | 1908 | 79.5
| 1909 | -33.3324 | 109.2757 | -33.3409 | -33.3 | 1909 | 79.5417
| 1910 | -33.3409 | 109.1365 | -33.3494 | -33.3 | 1910 | 79.5833
| 1911 | -33.3494 | 108.9974 | -33.3578 | -33.4 | 1911 | 79.625
| 1912 | -33.3578 | 108.8586 | -33.3663 | -33.4 | 1912 | 79.6667
| 1913 | -33.3663 | 108.7199 | -33.3748 | -33.4 | 1913 | 79.7083
| 1914 | -33.3748 | 108.5814 | -33.3832 | -33.4 | 1914 | 79.75
| 1915 | -33.3832 | 108.4431 | -33.3916 | -33.4 | 1915 | 79.7917
| 1916 | -33.3916 | 108.3049 | -33.4 | -33.4 | 1916 | 79.8333
| 1917 | -33.4 | 108.1669 | -33.4085 | -33.4 | 1917 | 79.875
| 1918 | -33.4085 | 108.0291 | -33.4168 | -33.4 | 1918 | 79.9167
| 1919 | -33.4168 | 107.8915 | -33.4252 | -33.4 | 1919 | 79.9583
| 1920 | -33.4252 | 107.7541 | -33.4336 | -33.4 | 1920 | 80
| 1921 | -33.4336 | 107.6168 | -33.442 | -33.4 | 1921 | 80.0417
| 1922 | -33.442 | 107.4797 | -33.4503 | -33.5 | 1922 | 80.0833
| 1923 | -33.4503 | 107.3428 | -33.4587 | -33.5 | 1923 | 80.125
| 1924 | -33.4587 | 107.206 | -33.467 | -33.5 | 1924 | 80.1667
| 1925 | -33.467 | 107.0695 | -33.4753 | -33.5 | 1925 | 80.2083
| 1926 | -33.4753 | 106.9331 | -33.4836 | -33.5 | 1926 | 80.25
| 1927 | -33.4836 | 106.7968 | -33.4919 | -33.5 | 1927 | 80.2917
| 1928 | -33.4919 | 106.6608 | -33.5002 | -33.5 | 1928 | 80.3333
| 1929 | -33.5002 | 106.5249 | -33.5085 | -33.5 | 1929 | 80.375
| 1930 | -33.5085 | 106.3892 | -33.5168 | -33.5 | 1930 | 80.4167
| 1931 | -33.5168 | 106.2537 | -33.525 | -33.5 | 1931 | 80.4583
| 1932 | -33.525 | 106.1183 | -33.5333 | -33.5 | 1932 | 80.5
| 1933 | -33.5333 | 105.9831 | -33.5415 | -33.5 | 1933 | 80.5417
| 1934 | -33.5415 | 105.8481 | -33.5498 | -33.5 | 1934 | 80.5833
| 1935 | -33.5498 | 105.7133 | -33.558 | -33.6 | 1935 | 80.625
| 1936 | -33.558 | 105.5786 | -33.5662 | -33.6 | 1936 | 80.6667
| 1937 | -33.5662 | 105.4441 | -33.5744 | -33.6 | 1937 | 80.7083
| 1938 | -33.5744 | 105.3098 | -33.5826 | -33.6 | 1938 | 80.75
| 1939 | -33.5826 | 105.1756 | -33.5907 | -33.6 | 1939 | 80.7917
| 1940 | -33.5907 | 105.0416 | -33.5989 | -33.6 | 1940 | 80.8333
| 1941 | -33.5989 | 104.9078 | -33.6071 | -33.6 | 1941 | 80.875
| 1942 | -33.6071 | 104.7742 | -33.6152 | -33.6 | 1942 | 80.9167
| 1943 | -33.6152 | 104.6407 | -33.6233 | -33.6 | 1943 | 80.9583
| 1944 | -33.6233 | 104.5074 | -33.6315 | -33.6 | 1944 | 81
| 1945 | -33.6315 | 104.3743 | -33.6396 | -33.6 | 1945 | 81.0417
| 1946 | -33.6396 | 104.2413 | -33.6477 | -33.6 | 1946 | 81.0833
| 1947 | -33.6477 | 104.1085 | -33.6558 | -33.7 | 1947 | 81.125
| 1948 | -33.6558 | 103.9759 | -33.6638 | -33.7 | 1948 | 81.1667
| 1949 | -33.6638 | 103.8434 | -33.6719 | -33.7 | 1949 | 81.2083
| 1950 | -33.6719 | 103.7111 | -33.68 | -33.7 | 1950 | 81.25
| 1951 | -33.68 | 103.579 | -33.688 | -33.7 | 1951 | 81.2917
| 1952 | -33.688 | 103.4471 | -33.6961 | -33.7 | 1952 | 81.3333
| 1953 | -33.6961 | 103.3153 | -33.7041 | -33.7 | 1953 | 81.375
| 1954 | -33.7041 | 103.1837 | -33.7121 | -33.7 | 1954 | 81.4167
| 1955 | -33.7121 | 103.0522 | -33.7201 | -33.7 | 1955 | 81.4583
| 1956 | -33.7201 | 102.9209 | -33.7281 | -33.7 | 1956 | 81.5
| 1957 | -33.7281 | 102.7898 | -33.7361 | -33.7 | 1957 | 81.5417
| 1958 | -33.7361 | 102.6589 | -33.7441 | -33.7 | 1958 | 81.5833
| 1959 | -33.7441 | 102.5281 | -33.7521 | -33.8 | 1959 | 81.625
| 1960 | -33.7521 | 102.3975 | -33.76 | -33.8 | 1960 | 81.6667
| 1961 | -33.76 | 102.267 | -33.768 | -33.8 | 1961 | 81.7083
| 1962 | -33.768 | 102.1368 | -33.7759 | -33.8 | 1962 | 81.75
| 1963 | -33.7759 | 102.0066 | -33.7839 | -33.8 | 1963 | 81.7917
| 1964 | -33.7839 | 101.8767 | -33.7918 | -33.8 | 1964 | 81.8333
| 1965 | -33.7918 | 101.7469 | -33.7997 | -33.8 | 1965 | 81.875
| 1966 | -33.7997 | 101.6173 | -33.8076 | -33.8 | 1966 | 81.9167
| 1967 | -33.8076 | 101.4878 | -33.8155 | -33.8 | 1967 | 81.9583
| 1968 | -33.8155 | 101.3585 | -33.8233 | -33.8 | 1968 | 82
| 1969 | -33.8233 | 101.2294 | -33.8312 | -33.8 | 1969 | 82.0417
| 1970 | -33.8312 | 101.1005 | -33.8391 | -33.8 | 1970 | 82.0833
| 1971 | -33.8391 | 100.9717 | -33.8469 | -33.8 | 1971 | 82.125
| 1972 | -33.8469 | 100.843 | -33.8548 | -33.9 | 1972 | 82.1667
| 1973 | -33.8548 | 100.7146 | -33.8626 | -33.9 | 1973 | 82.2083
| 1974 | -33.8626 | 100.5863 | -33.8704 | -33.9 | 1974 | 82.25
| 1975 | -33.8704 | 100.4581 | -33.8782 | -33.9 | 1975 | 82.2917
| 1976 | -33.8782 | 100.3302 | -33.886 | -33.9 | 1976 | 82.3333
| 1977 | -33.886 | 100.2023 | -33.8938 | -33.9 | 1977 | 82.375
| 1978 | -33.8938 | 100.0747 | -33.9016 | -33.9 | 1978 | 82.4167
| 1979 | -33.9016 | 99.9472 | -33.9094 | -33.9 | 1979 | 82.4583

## Sheet1 (hidden)
Newton's Method
Temperature difference between anbody and the durroundings. If not too larde, the rate of heat ransfer by all modes is approximately proportional to the temperature difference.
Tt=Tsur + (T0 - Tsur)e-rt
Tt | Final Temp
Tsur | Ambient Temp
T0
t